SUPPLEMENT TO

SPECIFICATIONS FOR

ELECTRICAL INSTALLATIONS

SERVICE ABOVE 15,000 VOLTS

ELECTRIC SYSTEM BULLETIN No. 752

OCTOBER 1994, 2ND PRINTING APRIL 2002

(Supersedes issue dated June 1985 and incorporates Nov. 1999 Errata List)

ESB752-1994 2nd Printing 2002.doc/SEIC/mb

TABLE OF CONTENTS

Section	Page

I.	INTRODUCTION	4

A.   PURPOSE	4

B.   SCOPE		4

C.   CUSTOMER'S RESPONSIBILITY	4

D.   COOPERATION	4

E.	CODES, STANDARDS AND WIRING ADEQUACY	5

F.	INSPECTION	5

G.   COMPLIANCE	6

4.	Required Documents and Submission Process	6

II.	DEFINITIONS	9

III.  GENERAL	9

A.   ACCESS	9

IV.   SERVICE CONNECTIONS	9

A.   GENERAL	9

B.   OVERHEAD SERVICE CONNECTIONS	9

C.   UNDERGROUND SERVICE CONNECTIONS	9

D.   PHASE DESIGNATION	9

E.	CONDUIT	10

V.   CUSTOMER SERVICE EQUIPMENT	10

A.   STATION REQUIREMENTS	10

1.	Electrical Short Circuit Capability	10

2.	Structural Design	10

3.	Structural Materials	10

4.	Foundation	10

5.	Oil filled Equipment	11

6.	Grading	11

7.	Surfacing	11

8.	Insulators and Connections	11

9.	Station Fence or Wall	11

10.   Signs	12

11.   Illumination	12

12.   Lightning Masts	12

B.   SWITCHES & SWITCHGEAR	12

1.	Disconnecting Switches	12

3.	Panic Hardware	13

C.   LIGHTNING ARRESTERS	13

D.   FAULT PROTECTION EQUIPMENT	13

3.	Power Fuses	13

4.	Circuit Breakers	14

5.	High Voltage Fault Interrupter	14

E.	POWER TRANSFORMERS	15

1.	Specification	15

2. Voltage Regulation	15

3.	Grounding	15

4.	Bushing Connections	15

5.	Current Transformers	15

F.	PROTECTIVE RELAYS AND COORDINATION	15

6.	Phase Designation Coordination	16

7.	Specific Relays	16

8.	Location of Relays	16

9.	Relay Test Facilities	16

April 2002	2	ESB 752-1994, 2nd Printing

TABLE OF CONTENTS (cont'd)

Section	Page

10.   Control Wiring	17

11.   Exclusion of Current Transformer Selector Switches	17

G.   OPERATION AND MAINTENANCE REQUIREMENTS	17

1.	General Requirements	17

2.	Specific Requirements	18

3.	Switching	18

4.	Maintenance	19

VI.   GROUNDING	20

A.   GROUND GRID	20

6.	Ground Grid Resistance	20

B.   CONNECTIONS TO GROUND GRID	21

5.	Switches	21

VII.	METERING	22

A.   EQUIPMENT FURNISHED BY THE COMPANY	22

B.   CUSTOMER'S RESPONSIBILITY	22

1.	Meter Equipment Mounting	22

2.	Secondary Connection Conduit	22

3.	Meter Panel Specification	23

4.	Meter Panel Location	23

C.   REMOTE METERING	24

Figures

1	Application Diagram Electrical Clearances

2	Outdoor Structure Electrical Clearances

3	Safety Clearance Requirements

4	Indoor Structure Electrical Clearances

5	Station Grounding

6	Switch Mechanism Grounding

7	Fence Grounding Details

7A	Alternative Fence Grounding Details

8	Meter House

9	Symbols for Service Equipment Diagrams

Illustrations

1	Typical 34.5kV Station

2	Typical 115kV Station

ESB 752-1994 2nd Printing	3	April 2002

I.	INTRODUCTION

A.	PURPOSE

1.	This Supplement to Electrical System Bulletin (ESB) #750 provides general

requirements and recommendations for a Customer who is or will be supplied by a Niagara Mohawk, a National Grid Company (Company) designated voltage in excess of 15,000 volts.

2. 	Additional information specific to the particular installation will be furnished upon

determination of the station arrangement and station location as mutually agreed upon by the Customer and the Company.

3.	It is important that the Customer and their engineer or contractor obtain and

refer to the Specifications for Electrical Installations booklet (ESB #750, latest

revision) in conjunction with this supplement.

B.	SCOPE

1.	These requirements are a guide to the Customer in making electrical installations

where the Company designates service voltage above 15,000 volts. The proper application of this guide will provide satisfactory service compatible with the electrical supply to others served by the Company System.

2. 	These requirements do not cover the Customer's complete electrical installation

design, but concern only those points in which the Customer, architect, their 
consulting engineer, electrical contractor, and the Company have a mutual interest.

3.	The Company furnishes the incoming line either overhead or underground to the

Customer's electric station.

4.	The Customer furnishes the complete electric station.

C.	CUSTOMER'S RESPONSIBILITY

1.	The Customer shall obtain building permits and/or zoning variances as required for

construction.

2. 	The Customer shall be responsible to ensure that provisions are included in any

station design for possible future expansion to accommodate additional Company interconnections, additional Customer interconnections or leads, and additional breaker, transformer or switching capability.

3.	The Customer shall be responsible to have all electrical and physical design

documents prepared by a design professional, in accordance with Section 1.7 of

ESB 750, and as further detailed later in Section I.G of this bulletin.

D.	COOPERATION

1.	For a specific electric service installation, it is essential that the Company meet with

the Customer, their consulting engineer, contractor or equipment manufacturer to mutually establish the arrangement and location of the proposed facilities.  As a result of this meeting,

a.  The Customer will provide the Company with a single line diagram and station 
	location plan.

b.  The Company will designate the supply voltage and provide available fault 
	values to the Customer.

April	2002	4	ESB 752-1994, 2nd Printing

2.	If the Customer makes changes in the design or scheduling of the project, then any

previous specific information furnished by the Company shall be subject to review and possible change by the Company.

3. 	The information the Customer or their contractor furnishes to the Company in

regard to the Customer's proposed electrical installation shall be in writing.

4. 	The complexity of modern electrical installations makes it essential that there be

continuous close cooperation between all parties involved.

5. 	It is the Company's desire to assist the Customer in understanding details of their

electric service installation.  When the information is not in this booklet, the Company invites inquiries from the Customer, their consulting engineer, their electrical contractor or their equipment manufacturer.

6.	The  Company's  Consumer  Relations  Department  will  advise  the  Customer

concerning any contribution which may be required of them for materials supplied

and work performed by the Company.

E.	CODES, STANDARDS AND WIRING ADEQUACY

1.	The Customer's electric service equipment and its installation shall conform to the

requirements of the latest edition of the National Electrical Safety Code, National

Electrical Code (where Applicable), and all governmental ordinances, building

codes and Company requirements and specifications.

2.	Components shall conform to the latest editions of the following national standards

and codes:

Component	Applicable National Standard

Cable	ICEA

Power Switchgear	ANSI  C37

Power and Instrument Transformers	ANSI  C57

Lightning Arresters	ANSI  C62

Insulators	ANSI  C29

Apparatus Bushings	ANSI  C76

Grounding	IEEE	80

3.	The Customer, their engineer, contractor and supplier should aim to provide a

modern, adequate electrical installation with ample provision for future needs.

4.	IEEE Standard No. 1109 "Guide for the Interconnection of User-owned Substations

to Electric Utilities" is a publication that could be helpful.

F.	INSPECTION

1.	To protect the Customer's interest, as well as its own, the Company requires the

Customer  to  furnish  satisfactory  evidence  from  the  local  authority  having jurisdiction as to the safe condition of their entire electrical installation before energizing the service to a new installation or re-energizing a service that has been disconnected for more than twelve (12) months.

2. 	This may be in the form of an approval or certificate from the New York Board of

Fire Underwriters, Factory Insurance Association, Factory Mutual Fire Insurance Company or other inspection organizations acceptable to the Company.

3.	Catastrophic occurrences such as fire, flood, etc. shall require a new certificate as to

the safe condition of the entire electrical installation before re-energizing.

ESB	752-1994 2nd Printing	5	April 2002

4.	Application for inspection should be made before the work is started.

5.	When significant station alterations are made, a new approval or certificate is

required to assure compliance with safety requirements.

G.	COMPLIANCE

1.	THE    CUSTOMER    SHALL    SUBMIT    THEIR    PLANS    AND

SPECIFICATIONS   TO   THE   COMPANY   BEFORE   ORDERING

EQUIPMENT OR STARTING WORK to insure that the proposed design for the

electric service installation conforms to Company requirements.

2.	Before an order is placed for electrical equipment, three copies of the Customer's or

manufacturer's specifications shall be furnished to the Company for review and

acceptance.

3. 	Review and acceptance by the Company shall not be construed to be a certification

of the Customer's facilities.  The Customer must obtain approval from a certified inspection agency.

4.	Required Documents and Submission Process

The required delivery of the design documents shall be as described in submittal 
stages “a”  through “d” below.   Drawings shall  be  originals prepared by the

Customer’s retained design professional and comprehensively detail the design of the electrical facility on a single sheet to permit full interpretation and understanding of all aspects.  The drawings shall be prepared in conformance with ANSI Y32.2, IEEE 141 and IEEE 446 symbol and drafting nomenclature.  All devices specified shall be of power utility grade and not industrial grade.

In order to speed and efficiently facilitate review, no portion of a submission should 
be sent until every element of the package is complete, final and deliverable in a 
single package in any of the following stages. Unless otherwise requested and at the 
sole discretion of the Company, no individual document, or partial design, of a 
submission will be accepted for Company review until the Customer has declared 
that the package is complete.  In all instances, six (6) complete sets of design 
documents shall be submitted for Company review and acceptance.

a.  PRELIMINARY SUBMITTAL

Plot plan

Functional  single  line  diagram  with  proposed  ratings  of  disconnecting devices, over current protection, transformer size and impedance.

b.  DETAILED ELECTRICAL DESIGN SUBMITTAL

Complete functional single line detailing all devices up to, and including, the Customer’s secondary protective device.  It should include: all protective relays  in  sufficient  detail  to  show  intended  operation;  all  instrument transformers with ratios, including excitation curves; power and station service transformers with ratios; etc.

List of proposed relay settings based on a formal relay coordination study. Settings shall not be shown on drawings.

Electrical AC ELEMENTARY in sufficient detail to show the functional 
control operation of the station.  The elementary schematic diagram shall 
be in three-line format and show, by means of graphic symbols, all devices

April	2002	6	ESB 752-1994, 2nd Printing

having any interaction with the tripping function of the main protective 
device.  Specifically, it shall include all individual items of equipment, 
devices within the equipment, their coils, contacts, windows, terminals, 
AC source, and each connection (wire, cable or bus) between equipment 
and devices.

Electrical  DC  ELEMENTARY,  if  required  by  protective  device,  in 
sufficient detail to show the functional control operation of the station. 
The D.C. elementary schematic diagram shall show, by means of graphic 
symbols, all devices having any interaction with the tripping function of 
the main protective device.  Specifically, it shall include all individual 
items of equipment including batteries, battery charger, devices within the 
equipment, their coils, contacts, windows, terminals, and each connection 
(wire, cable or bus) between equipment and devices. (Note - Ladder-type

diagrams are not acceptable.)

Structural detail and foundation drawings of the high voltage receiving 
point.

Assembly plan and elevation details of the high voltage station and its safety structures including grounding plans.

Meter conduit drawings

Control house layout 
Relay panel drawings

Material lists of major components

Transformer nameplate and outline drawings

Main disconnect switch nameplate, showing ratings and certifications

Equipment specifications for lightning arresters; power fuses; main high 
voltage interrupter or breaker; main disconnect switch; switchgear; power 
transformer

c. 	FINAL, FOR-CONSTRUCTION SUBMITTAL

A complete set of all drawings and equipment specifications outlined above, marked final/for construction.  Also, at this time the manufacturer’s test reports for the power transformer and circuit breaker or high voltage interrupter shall be submitted.  This is the end of the design process.  The full set of design professional sealed final documents shall then be submitted with the service application for review in total by the Company.

d. 	FINAL, AS-BUILT IN FIELD SUBMITTAL

Once construction is complete and the service energized, a full set of the drawings in item c above shall be submitted within 90 days.  They shall accurately document the as-built status of the project, including any deviation from the final for-construction design drawings, and again be sealed by the Customer’s design professional.

5.	Proposed location and arrangement of Company metering equipment shall be shown

on drawings submitted.

6.	Relay diagrams shall always show relay contacts in the de-energized position.

ESB	752-1994 2nd Printing	7	April 2002

7.	The Company will issue written instructions on operating procedures for the

Customer's service equipment directly involved with the Company's system.  These 
instructions shall be followed in all operations involving the Customer's service 
equipment.

8. 	The following conditions are to be performed and/or maintained by the Customer's

contractor while working in the vicinity of the Company's overhead lines. This list shall be noted on the Customer's design drawings and posted at the work site.

a. 	No personnel or equipment or combination thereof shall come closer than the

following distances to any energized conductor: 	(From New York State High

Voltage Proximity Act - 1989.)

600V < 50kV	>50kV<115kV	230kV	345kV

10 ft.	15 ft.	17 ft.	20 ft.

b.	Equipment which is operated in the direct vicinity of the overhead lines shall be

effectively grounded.

c. 	Equipment which has the capability of extending within the wire clear zone

established above shall have a warning sign attached identifying the potential 
hazard.

d. 	No equipment utilized in site preparation grading, etc. shall be operated within

ten (10) feet of any electric line supporting structure.

e.	There shall be no changes in grade within the Company's Right-of-Way unless

approved by the Company.

f.	There shall be no excavation under the overhead lines within 15 feet of the

nearest wood member or guy anchor and/or 25 feet of the nearest steel member

of an electric line supporting structure.

g.	All spoil not used to backfill the excavation  shall  be  removed  from the

Company's Right-of-Way.

h.	There shall be no blasting on the Company's Right-of-Way.

i.	The site preparation procedures shall include no activities which cause material

to flow off of the Company's Right-of Way.

j.	No activities shall be permitted which compromise the electrical or structural

integrity of the overhead electric facilities.

k.	No activities shall be permitted which prevent or inhibit the Company from

exercising reasonable ingress and egress along the Company's Right-of-Way.

l.	The Company reserves the right to review and inspect for its purposes any

construction drawings, specifications, and activities being carried on within the

Company's Right-of-Way.

9.	See Figures 1-4 for required electrical installation clearances.

10.	The  Company reserves  the  right  to  review  and  inspect  the  installation  as  it

progresses.

11.	An  authorized  representative  of  the  Company  will  examine  the  Customer's

installation before it is energized to insure compliance with these specifications.

April 2002	8	ESB 752-1994, 2nd Printing

II.	DEFINITIONS

Note:  Definitions as used in this specification are provided in the "Specifications for

Electrical Installations" book (ESB#750), Section 2.

III.	GENERAL

A.	ACCESS

1.	Arrangements shall be provided so that authorized Company employees may have

access to the Customer's substation, switching facilities and metering at any time

and without delay.

2.	A suitable  driveway  shall  be  provided  by  the  Customer  to  permit  truck  or

maintenance vehicle access to the station area. This driveway should be adequate to

handle a crane and lowboy truck, if necessary, without additional work.

IV.	SERVICE CONNECTIONS

A.	GENERAL

1.	The Customer shall provide a suitable receiving structure for attachment of the

Company's line, this attachment is the defined "service point."

2.	The Company will provide a cable to flat terminal connector to connect the

Company's line to the Customer's equipment.

3.	Service voltages above 15kV are unregulated.  Voltage excursions of +10% are

possible.   The  Customer  shall consider  the  installation  of  their  own  voltage

regulation equipment if necessary.

4.	The Customer shall consult with the Company regarding right-of-way easements

required between the Company's line and the Customer's station.

B.	OVERHEAD SERVICE CONNECTIONS

1.	The Company will provide the incoming line dead end clamps, insulators, and

clevises for attachment of the Company's overhead line to the Customer's structure.

2. 	The Customer shall provide a suitable structural member for attachment of the

Company's hardware.  This structural member shall have a hot dipped galvanized 
steel dead-end tee bracket mounted at each incoming conductor attachment point. 
This bracket shall have 13/16" mounting holes on 6" centers and the tab shall have a 
1" diameter hole with no less than 1-½" of material from the edge of the hole to the 
edge of the tab.

C.	UNDERGROUND SERVICE CONNECTIONS

1.	The Company will provide the incoming cable and terminations for attachment of

the Company's underground line to the Customer's equipment.

D.	PHASE DESIGNATION

1.	Phase Designation and Sequence

a.  All the Company service circuits have the line leads designated with the phase 
	numbers 1, 2 and 3.

b.  The Company will identify the phase number for each conductor at the point of 
	connection of the service circuit to the Customer's equipment; the Customer 
	shall mark their equipment accordingly.

ESB	752-1994 2nd Printing	9	April 2002

c.  The phase sequence is 1-2-3 and rotation is counter-clockwise.

E.	CONDUIT

1.	Any conduit required for control circuits, metering circuits or power circuits shall be

furnished, installed, owned and maintained by the Customer. It shall be installed at

the following minimum depths:

Control circuits	- 18"

Metering circuits	- 18"

Power circuits below 600 V	- 18"

Power circuits above 600 V	- 30"

2.	The conduit layout shall be approved by the Company before installation.

3.	The installation of spare conduits is recommended.

4.	Frost effects shall be taken into consideration when designing underground conduit

layouts.

V.	CUSTOMER SERVICE EQUIPMENT

A.	STATION REQUIREMENTS

1.	Electrical Short Circuit Capability

The station equipment shall be suitable for the maximum fault current available at 
its supply terminals. The Company will provide the expected fault values available 
less the Customer contribution. Consideration for future system or load growth may 
require initial installation of service equipment having a larger interrupting rating.

2.	Structural Design

a.  Clearances:

(1) Standard electrical clearances shall be maintained, see Figures 1, 2, 3 and 4.

(2) Appropriate normal and minimal electrical clearances from energized parts 
	above walkways, roads, and railroads and in other special circumstances are 
	specified in the latest editions of ANSI C2 and IEEE Std. 1119.

(3) All clearances shall conform to state and local codes and ordinances.

b.  Line Tensions:

(1) The  structures  shall  be  designed  to  withstand  the  conductor  tensions 
	specified by the Company without exceeding the stresses specified in the 
	latest NEMA Standard SG-6 or latest superseding publication.

(2) Minimum tensions, spacings and heights for the service conductor attach-
	ments will be provided by the Company for each installation.

3.	Structural Materials

a.  It is recommended that the substation structure be constructed of galvanized

structural steel conforming to NEMA and ANSI Standards.

b.  Structures of other materials may be accepted if adequately designed.

4.	Foundation

a.  Foundation piers for the substation structure shall extend below the frost line

and  shall  withstand  the  overturning  moment  resulting  from  the  specified

April	2002	10	ESB 752-1994, 2nd Printing

conductor tension and wind loads.

b.  Foundations for transformers and other apparatus may be of the slab type resting 
	on 12" of #2 crushed stone.  Soil pressures appropriate to the soil conditions in 
	the station area shall be used in designing foundations.

5.	Oil filled Equipment

a.  Spacing of oil filled equipment - the Customer should use NFPA 850 as a guide 
	and consult their insurance carrier for separation requirements.

b.  Oil Containment

(1) The station must be designed and installed to comply with Title 40, Code of 
	Federal Regulations, Part 112 "Oil Pollution Prevention" (40CFR112).

(2) Compliance to 40CFR 112 shall be verified in writing by the Customer's 
	engineer from transformer design data and design data for any other oil-
	filled electrical equipment at the station facility.

c.  For further guidance on fire prevention and oil-spill containment, see IEEE Std. 
	979 and IEEE Std. 980.

6.	Grading

a.  The rough grade of the substation site should have a minimum slope of 1" in 10', 
	sloped toward drainage ditches or tile designed to carry the runoff of surface 
	water.

b.  The design should insure a dry surface throughout the substation area.

7.	Surfacing

The area of the substation, including 3' outside of the fence, should be surfaced with at least 6" of #2 crushed stone.

8.	Insulators and Connections

a.  All power connections shall be adequately supported to resist the mechanical 
	stresses including those imposed by short circuit current equal to the interrupting 
	current rating of the circuit protective means.

b.  Where,  because  of  atmospheric  contamination  or  for  other  reasons,  the 
	Customer's station switch insulators or bushings are rated for voltage higher than 
	actually supplied, appropriate coordinating gaps shall be installed.

9.	Station Fence or Wall

a.  At a minimum, outdoor installations shall be protected by an 8' high (minimum) 
	grounded wire mesh fence. This fence shall consist of at least 7' high wire fabric 
	of at least #9 gauge galvanized wire, 2" mesh, topped by 3 strands of barbed 
	wire; and such gates, removable sections, etc. as necessary.

b.  Other fence materials or walls may be substituted where approved by the 
	Company.

c.  All gates shall be provided with hasps with provisions for Customer and 
	Company padlocks so that only authorized persons have access into the fenced 
	area. Refer to Figure #3 for safety clearance to fence.

ESB 752-1994 2nd Printing	11	April 2002

10.	Signs

a.  The Customer shall provide signs, 12" x 17", installed on the outer sides of the 
	station fence with maximum of 50 feet apart or minimum of one on each side 
	and rear of fenced area, all personnel and vehicle gates, and on all entry doors to 
	station control rooms, each sign reading in large legible letters, "DANGER -
	High Voltage Within - Keep Out - Access Restricted to Qualified Persons 
	Only".

b.  In addition, there shall be a 20" x 28" sign mounted on the fence gate which 
	reads, "DANGER, Private Property, No Trespassing".

11.	Illumination

a.  The Customer shall provide suitable illumination for the substation area.

b.  Appropriate minimum lighting levels for various circumstances of indoor, 
	outdoor, and roadway areas are given in the latest editions of NFPA 70 and 
	ANSI C2.

c.  Emergency lighting shall be provided in attended areas in accordance with local 
	codes and regulations.

12.	Lightning Masts

a.  The  substation  structure  shall  be  equipped  with  suitable  lightning  masts 
	providing the necessary cone of protection.  The "rolling sphere" method is 
	acceptable for shielding against direct lightning strokes using a 250 ft. radius 
	sphere.

b.  Other lightning protection measures may include:

shield wires, arrays, arresters, higher BIL levels, etc. However, overhead ground wires are not to be used over station equipment.

c.  For more information on direct stroke lightning protection, see NFPA 780.

B.	SWITCHES & SWITCHGEAR

1.	Disconnecting Switches

a.  One vertical break disconnecting switch shall be provided for each service 
	circuit at the point where the service circuit attaches to or enters the Customer's 
	station.

b.  This switch shall be three pole, single throw, gang operated.

c.  The  switch  shall  be  in  accordance  with  ANSI  Standard  C37 	for  Power

Switching Equipment, NEMA and UL guidelines.

Note: The ice test shall pass for 1/2" ice loading, NESC Heavy.

d.  The switch mechanism may be manually or electrically operated.

e.  This mechanism shall be provided with a means for locking in both open and 
	closed position.

f.  The operating handle shall be grounded and connected to a potential equalizing 
	grid.

g.  It is recommended that where the station arrangement makes it practical, the

April	2002	12	ESB 752-1994, 2nd Printing

switch operating mechanism should be interlocked with the circuit breaker or fault interrupter so that the switch will not be used to interrupt load current.

h.  Where the switch may be used to interrupt transformer magnetizing current, a 
	load break switch may be required.

i. 	For outdoor installations, this switch shall be horizontally upright mounted.

(1) The switch should be a vertical break rotating insulator type with three 
	insulator stacks per pole.

(2) The switch shall be complete with arcing horns.

(3) All non current carrying metal parts should be either hot-dipped galvanized 
	steel or corrosion resistant material of adequate strength.

(4) Other types of switches may be acceptable with prior Company approval.

j. 	Insulators shall be of the porcelain (ceramic) type; other types may be acceptable

with prior Company approval.

k.  After installation and before being energized, the switch must be thoroughly 
	operationally tested in accordance with manufacturer's instructions.

2. 	Construction of the switchgear control building shall conform to National Fire

Protection Association (NFPA), U.L., and all local fire codes.

3.	Panic Hardware

a.  Doors to switchgear rooms or walk-in metal clad switchgear shall be equipped

with panic hardware.

b.  The lock preventing access to these rooms shall not prevent egress.

C.	LIGHTNING ARRESTERS

1.	Recommended lightning arrester voltage rating in kV MCOV and type will be

provided by the Company.

2.	Lightning arresters should normally be connected on the load side of the service

disconnecting switch.

3.	Where lightning arresters must be connected on the supply side of the service

disconnecting switch, each arrester shall be provided with a separate isolating

switch.

4.	Lightning arresters shall be mounted so that their bases are a minimum of 8'-6"

above grade or floor level; otherwise, a suitable guard fence or metal enclosure shall

be provided around them.

D.	FAULT PROTECTION EQUIPMENT

1.	Fault protection equipment shall be designed for the maximum voltage rating of the

service and shall be capable of interrupting the maximum short circuit current 
available from the system to isolate a short circuit from the supply, see Figure 2.

2. 	Circuit interrupting devices containing flammable materials shall be adequately

segregated from other equipment and buildings to limit damage in the event of an explosion or fire, see ANSI C2 NESC.

3.	Power Fuses

a.  Where fuses are applicable for protection of service installations and are desired

ESB	752-1994 2nd Printing	13	April 2002

by the Customer, their rating and time-current characteristics will be specified by the Company to coordinate with the supply system protective equipment.

b.  Substitution of any fuse, other than that specified, must have Company approval.

c.  The Customer should maintain a stock of at least four spare fuses, a spare set of 
	fuse clips, and fuse or switch operating poles as required; all in an accessible dry 
	storage space.

4.	Circuit Breakers

a.	Circuit breakers used in service installations shall be three pole and of a rating

acceptable to the Company.

b.	Breakers  may  be  oil  or  oil-less  type	(such  as  vacuum  or  SF6	(Sulfur

Hexafluoride) gas-insulated).

c.	Breakers shall be in accordance with latest ANSI Standard C37 for Power

Circuit Breakers.

d.	It is recommended that circuit breakers be tripped by direct current supplied

from a battery.

(1) Such a battery shall be rated not less than 48 volts, with ampere hour 
	capacity suitable for the application.

(2) Facilities shall be provided to maintain the battery in a fully charged 
	condition.

(3) Capacitor trip devices are not acceptable.

e. 	The Customer's circuit breaker source side bushings shall be equipped with

current transformers having characteristics as specified by the Company to 
supply  protective  relays  associated  with  the  circuit  breaker. Potential

transformers may also be required.  Relay data and transformer ratios shall be marked on the single line diagram.

f. 	The use of bypass switches around protective devices is not permitted.

Note:  Using a transfer breaker and transfer bus can avoid this concern.

5.	High Voltage Fault Interrupter

a.  In locations where system conditions would normally require installation of a 
	circuit breaker, the use of other types of fault interrupters may be approved by 
	the Company.

b.  The fault interrupter shall be furnished with a control pack approved by the 
	Company. The motor and control voltage shall not be less than 48 volt D-C.

c.  Where a fault interrupter is provided, the source side bushing of each phase of 
	the Customer's power transformer shall be equipped with current transformers.

(1) These current transformers shall be the source for the relays which will 
	actuate tripping of the fault interrupter.

(2) The relay data and current transformer ratio shall be marked on the single 
	line diagram.

d.  Where a fault interrupter is provided, a remotely located Company line circuit 
	breaker will normally interrupt faults in excess of the fault interrupter rating.

April	2002	14	ESB 752-1994, 2nd Printing

e.  The Customer, in selecting this type of protection, runs the sole risk and 
	responsibility for damage to their own equipment as would be the case if they 
	supplied their own main circuit breaker.

E.	POWER TRANSFORMERS

1.	Specification

Power transformer specifications shall be mutually agreed upon by the Customer and Company in accordance with nationally accepted standards.

2.	Voltage Regulation

a.  Voltage taps should be specified to best deliver the rated low voltage over the 
	range or normal system operating voltages.

b.  The Customer should consider the use of regulators or transformers with load 
	tap changing equipment if critical voltage control is required for their facility.

3.	Grounding

a.  It is the Customer's responsibility to specify the method for grounding the 
	transformer secondary neutral, i.e. - solidly grounded, resistance grounded,

impedance grounded, or ungrounded.

b.  The Customer shall furnish, install, own and maintain any grounding equipment.

4.	Bushing Connections

a.  Connections to power transformers shall be non-rigid to guard against undue 
	thermal or mechanical stress on transformer bushings.

b.  Adequate cable support is required to prevent undue stress on the transformer 
	bushings.

5.	Current Transformers

a.  For test purposes to pass current, current transformers in the Customer's power 
	transformer neutral circuit shall be externally mounted. This applies to the 
	neutral only.

b.  Neutral current transformers shall be located on the transformer side of the 
	resistors or reactors etc., and shall be rated for full line-to-neutral voltage.

F.	PROTECTIVE RELAYS AND COORDINATION

1.	The Customer or their authorized representative shall be responsible for the proper

installation, adjustment and operation of protective relays and switchgear including periodic test procedures, as outlined in NFPA 70B - Electrical Equipment Maintenance, to maintain proper operation of service entrance equipment.

2. 	The Company may require some of these tests to be performed by Company

personnel to insure coordination with the electrical supply system.

3. 	The Company will seal the designated relay devices listed on the Company-supplied

relay setting sheets, verify accuracy of associated circuit wiring, and perform a functional test of the required interrupting devices, i.e. trip test.

4.	Periodically, the Company will check the Company designated relay devices.  The

check will consist of a visual/mechanical examination of the designated required

relay devices, seals and associated wiring. If seals are broken, the protective devices

shall be recalibrated, tested and re-sealed.  Cost of corrections will be borne by the

ESB	752-1994 2nd Printing	15	April 2002

Customer.

5. 	The Customer is responsible for specifying the relay settings and performing the

calibration, testing, maintenance and trouble-shooting of the remainder of the Customer-owned protective system.

6.	Phase Designation Coordination

a.  Coordination of the Customer's low voltage phase designation with that of the 
	high voltage service circuit phase designation shall not be overlooked.

b.  Customer's  installation  layouts  shall  provide  phase  designations  fully 
	coordinated between high voltage and low voltage equipment.

c.  The Company will assist the Customer to this end, providing the Company 
	receives composite wiring diagrams from the high voltage service circuits to the 
	low voltage load circuits.

d.  Phase  designation  coordination  will  facilitate  checking  of  protective  relay 
	wiring,  testing of  relays,  and  proper  installation  and  operation  of  all  the 
	Customer's electrical facilities.

e.  Isolated, fragmented and individual wiring diagrams for units of the Customer's 
	installation are not sufficient for checking phase arrangement.

7.	Specific Relays

a.  The Company's minimum requirements and recommendations for protective 
	relay facilities for a specific electric service installation will be provided upon 
	submission of the single line diagram.

b.  If during the course of a project, changes and additions to the single line diagram 
	are identified, then such changes and additions shall be submitted to the 
	Company on a revised single line diagram for the Company's approval prior to 
	implementation or purchase of equipment.

8.	Location of Relays

a.  All relays for the Customer's service installation whose operation could affect 
	the Company's facilities should be readily accessible to authorized personnel of 
	both the Customer and the Company.

b.  Relays should be located so as to be free of dust, dirt, dampness and corrosive 
	atmosphere.

9.	Relay Test Facilities

a.  All protective relay connections shall be provided with suitable test points to 
	facilitate initial, as well as periodic check and calibration.

b.  Lockout auxiliary relays shall be provided with test devices.  Draw-out case 
	design relays with built-in test facilities are recommended.  If separate test 
	devices  are  used,  they  shall  be  General  Electric  type  PK-2 or  ABB

(Westinghouse) FT-1 test blocks with the wiring between the test block and the relay in accordance with Company standards.  Information on these standards will be provided when requested by the Customer.

c.  A 120/240 volt, 50 ampere, single phase, three wire, NEMA 10-50, convenience 
	receptacle (Hubbell #7963), or equal, located near the relay panel, shall be 
	provided for relay testing purposes.

April	2002	16	ESB 752-1994, 2nd Printing

d.  Where three phase relaying and/or metering will be installed, a three phase 
	100A, 208Y/120V source is required.

10.	Control Wiring

a.  DC control wiring in locations subject to dampness, for individual conductors, 
	shall be ICEA Class "B", 600 volt rated.

b.  All multiple conductor control cables shall be ICEA Class "C", 600 volts with 
	jacket thickness as specified by ICEA.

c.  Cable  systems  required  to  interconnect  protective  relaying,  metering, 
	instrumentation, control, communications, and low-voltage power equipment 
	systems should be in conformance with IEEE Std. 525.

d.  Supervisory Control - Customers who wish to use Supervisory Control and Data 
	Acquisition (SCADA)  systems  shall  follow  the  guidelines  set  forth  in 
	ANSI/IEEE Std. C37.1.

11. 	Exclusion of Current Transformer Selector Switches

a.  Meter selector switches or meters shall not be connected into the secondary 
	circuits of current transformers used with protective relays specified by the 
	Company.

b.  If separate metering current transformers cannot be provided, the metering must 
	be isolated by suitable saturating auxiliary current transformers.

G. 	OPERATION AND MAINTENANCE REQUIREMENTS

The following is in the mutual interest of the Company and the Customer where 
the Customer's service equipment is directly involved with the Company's System.

1.	General Requirements

a. 	The switching protocol procedure for the mutual interest of the Company and

the  Customer  will  be  provided  by the  Company based  on  the  following information from the Customer:

Contact personnel and telephone numbers and

Single-line diagram from Section I.G above of the Customer’s primary and secondary equipment directly involved with the Company’s system.

b. 	The Customer is responsible for maintaining this information up-to-date and

notifying the Company of any changes.

c. 	All switching within the Customer's service equipment above 15 kV, shall be in

accordance  with  Company  provided  customer  operating  instructions.  The Customer is responsible for developing operating instructions for the balance of their electrical system.

d. 	The Company can provide isolation and grounding guarantees at the Customer's

service disconnect or Company isolation point on the supply line ahead of the Customer's service equipment. However, the Customer is responsible for their grounding provisions to work on their de-energized equipment.

e. 	The Customer shall operate within established Company mark up rules in any

switching operations with the Company for their equipment that both the 
Company and the Customer have a mutual interest. It is expected the Customer

ESB	752-1994 2nd Printing	17	April 2002

will provide a qualified person as defined in the National Electrical Code and any other applicable codes.

f.  The Customer must recognize and abide by the Company's mark up rules. The 
	Customer shall conduct their switching based on their switching practices 
	insuring that the Company's mark up is not jeopardized or modified.

g.  References to minimum customer requirements for maintenance, operating, and 
	safety of their high voltage installation include but are not limited to:

NFPA 	70B   "Recommended   Practice   for   Electrical   Equipment Maintenance"

NETA-MTS "Maintenance Testing Specifications for Electrical Power Distribution Equipment and Systems"

NFPA 70E "Electrical Safety Requirements for Employee Workplaces" IEEE/ANSI C2 "National Electrical Safety Code"

OSHA 29 CFR 1910.269

2.	Specific Requirements

a.	Service Personnel and Safety:

The Customer is responsible for performing all switching and O&M functions for their equipment.

The Customer shall arrange to have qualified personnel available at all times for the proper and safe operation of their equipment.

"Qualified Personnel" training shall cover correct operating and safety procedures including, but not limited to:

distinguishing exposed live parts,

determining the nominal voltage of exposed live parts, 
determining of the minimum approach distance, and

the use of precautionary techniques, personal protective equipment, insulating and shielding materials, and insulated tools for working on or near exposed live parts of electrical equipment.

b. 	The Company does not provide any operating tools for the Customer's use.

The Customer shall provide their own operating equipment such as tongs, 
insulating switching sticks, insulated rubber gloves, grounds, ground bails, 
studs and grounding sticks; voltage detection equipment, etc. needed for the

safe performance of operating functions. This operating equipment shall be 
properly maintained and tested according to the manufacturer's instructions.

c. 	Line  terminations  and  the  metering  transformer  compartments  of  the

Customer's switchgear will be locked by the Company when the Company's work is completed and marked clear with the Controller.

3.	Switching

a.  All switching or other work on high voltage circuits shall be performed by

qualified personnel fully equipped with safety equipment tested for the circuit

voltage involved.

April	2002	18	ESB 752-1994, 2nd Printing

b. 	All Company directed switching within the Customer's station shall be done in

accordance with Company-provided switching instructions.

c. 	The Company will provide nomenclature for Customer's labeling of the main

disconnect switch and other electrical equipment referred to in the Company's switching instructions.  The Customer shall make provisions for the labeling of this equipment and any necessary mark-up tag holder.

d. 	Tags shall be used to prohibit operation of electrical devices and shall indicate

that  employees  are  at  work.  Equipment  shall  be  locked  and  rendered 
inoperable by locking and tagging unless its design does not so permit. Tags 
alone may be used when the equipment can not be rendered inoperable by 
locking.

e.	NO WORK SHALL BE DONE ON AN AIR BREAK SWITCH WHILE THE

INCOMING LINE IS ENERGIZED.

(1) Notify the Company and arrange for an interruption and a guarantee before 
	doing any work at or near this section. Also, if requested, a grounding 
	guarantee may also be requested.

(2) THE MAIN DISCONNECTING SWITCH SHALL BE LOCKED OPEN 
	PRIOR TO CHANGING FUSES OR WORKING ON HIGH VOLTAGE 
	EQUIPMENT.

(3) THE SAFETY PRECAUTIONS outlined in the NESC ANSI C2, OSHA 
	and local requirements shall be strictly adhered to. The Customer shall 
	ensure the circuit/equipment has been tested as deenergized and grounded 
	prior to work.

4.	Maintenance

a.	The  Customer  is  responsible  for  maintaining  all  equipment  under  their

ownership.

b.	Proper  preventative  maintenance  is  important  to  the  operation  of  the

equipment and shall be performed.

c. 	NFPA Standard No. 70B on "Electrical Equipment Maintenance" and NETA-

MTS "Maintenance Testing Specifications for Electrical Power Distribution 
Equipment and Systems" are two publications that could be helpful in setting 
up a dynamic maintenance program.  Copies of test records of major station 
equipment and protective devices that both the Company and the Customer 
have a mutual interest in shall be maintained on the premise and be made 
available to the Company upon request, e.g. breaker, transformer, outdoor 
switches, and relay devices.

d. 	The Company does not provide any spare parts for the Customer's installation.

The Customer should determine their inventory of spare parts for circuit breakers,  fault  interrupters,  switchgear,  and  other  electrical  equipment essential to minimize their interruption time.

e.	Customer access to Company controlled electrical spaces within Customer-

owned electric facilities:

The Company's control of electric spaces in Customer-owned electric facilities

is for the sole purpose of protecting the integrity of the Company's energy

supply and security of the utility metering equipment. Any costs shall be

ESB	752-1994 2nd Printing	19	April 2002

determined by the Company's filed tariff. In these requirements, "Customer" 
refers to the Customer or their agent. Under this and all other policies, it is 
expected and it is the Customer's responsibility to provide a qualified person 
as defined in the National Electrical Code and any other applicable codes.

(1) The Company can provide isolation and grounding guarantees at the 
	Customer's service disconnect or Company isolation point on the supply 
	line ahead of the Customer's service equipment. However, the Customer is 
	responsible for their grounding provisions to work on their de-energized 
	equipment.

(2) When the Customer does not require a guarantee on the supply line and 
	needs  access  to  Company-controlled  electrical  spaces  for  their 
	maintenance purposes, the Company in its sole judgment may determine 
	the ability to grant access to the Customer for the duration established by 
	the Company. When granted, the Company will witness the Customer's 
	placement of their lock immediately after the removal of the Company's 
	lock. Upon notification by the Customer that their work is complete, the 
	Customer shall relinquish access back to the Company and the Company's 
	lock shall be placed immediately upon the removal of the Customer's lock. 
	In each case the transfer shall occur in the presence of both parties.  The 
	Company will check it's electrical equipment for any signs of tampering.

In the event that the required access is of short duration and the Company's 
representative remains on site, to avoid a second trip, it is understood they are 
doing  so  without  any  supervisory  or  oversight  capacity  relative  to  the 
Customer.

VI.	GROUNDING

A.	GROUND GRID

1.	Normally, the substation ground grid design should conform to the requirements of

IEEE Std. 80.

2. 	The ground grid shall not be closer than 25 feet from any buried fuel lines.

However, some instances may require greater distances.  Consult the Company whenever buried fuel lines are in proximity to the station.

3.	The Customer shall install a ground grid of #4/0 bare stranded copper conductor or

as specified by the Company, connected to an earthing means such as driven ground

rods.

4.	Below grade connections shall be made with compression type connectors or by a

"Cadweld" or equivalent process.

5. 	For outdoor installations the ground grid shall form one or more closed loops, 18

inches below grade, surrounding the Customer's service equipment structure.  One loop must be installed 2'-6" outside of the fenced area and swing gate path(s).

6.	Ground Grid Resistance

a.  A ground resistance test should be conducted in accordance with IEEE Std. 81.

b.  The ground resistance of the ground grid shall be verified by the Company after 
	installation  by  the  Customer  prior  to  adding  cover  material (but  before

connection to water pipe or overhead line ground wire) using a Biddle ground 
tester, or by other suitable means, to be assured that the ground resistance is no

April	2002	20	ESB 752-1994, 2nd Printing

greater than the value specified by the Company.

7.	Connection of the ground grid to a continuous underground metallic water piping

system is recommended.

8.	When connection is made to a water piping system, the connection shall be made on

the source side of the water meter where possible. Otherwise, the water meter shall

be provided with a bonded by-pass.

B.	CONNECTIONS TO GROUND GRID

1.	The following components should be solidly connected to the ground grid using

#4/0 copper conductor minimum:

a.  Metallic conduits for power and control cables, including the entire run of 
	service lateral conduit if needed.

b.  Bonds for metallic cable sheaths and terminals.

c.  Metal supporting structures and frameworks.

d.  Lightning arresters and protective gaps.*

e.  Tanks of power transformers.

f.  Frames of circuit breakers and switchgear units.

g.  Overhead static shield wires.*

h.  Lightning masts.*

*Note: These items shall be connected separately to the ground grid.

2. 	All non-current carrying metallic parts of the Customer's installation shall be

adequately grounded to the grid.

3. 	Disconnecting switch bases, fuse mount bases, insulator supports, and instrument

transformer frames or cases are normally adequately connected to the ground grid through their mechanical fastenings and the supporting structure if the structure is metal. If these items are installed on a non-conductive structure, these items shall be suitably grounded.

4. 	All fences enclosing the Customer's station shall be continuously grounded by being

solidly connected to the ground grid using not less than #4/0 AWG bare stranded copper conductor, at all corner posts, at not more than 50 foot intervals around the fence perimeter and immediately on each side of gates or removable sections.  The gates themselves shall be grounded by a flexible copper braid.

5.	Switches

a.  Each group-operated air break disconnecting switch or fault interrupter device 
	remote operating mechanism shall be connected to the ground grid near the 
	operating handle by means of a flexible, tinned copper braid of at least 200 
	ampere rating.

b.  For outdoor installations a potential equalizing grid of buried copper grid 
	(typical grid shown by Figure 6 in rear of booklet) shall be placed at the foot of 
	the column supporting the operating mechanism.

c.  This potential equalizing grid shall be connected in two places to the switch 
	main grounding lead using at least #2 and preferably #4/0 bare stranded copper 
	conductor.

ESB	752-1994 2nd Printing	21	April 2002

d.  NOTE:

EVEN  WITH  THE  GROUND  PRECAUTIONS  SUGGESTED,  IT  IS IMPERATIVE THAT A PERSON OPERATING GROUP-OPERATED SWITCHES WEAR RUBBER GLOVES.

6.	A #2AWG bare stranded copper conductor (minimum) connection from the ground

grid shall be made available at the meter panel for use by the Company to ground

the billing meter equipment.

VII.	METERING

A.	EQUIPMENT FURNISHED BY THE COMPANY

1.	The Company will furnish all meters, metering instrument transformers, potential

transformer primary fuses and test devices required for billing purposes at the delivery voltage.

a.  Metering Transformers

(1) The Company will specify the quantity, type, rating and primary connections 
	of all current and potential transformers for billing purposes.

(2) The current and potential transformers for the Company's billing meters 
	shall not be used to operate any other devices.

b.  Potential Transformer Primary Fuses

(1) The Company will specify when potential transformer primary fuses are to 
	be used, together with the quantity, type, rating and connections of such 
	fuses and their mountings.

B.	CUSTOMER'S RESPONSIBILITY

1.	Meter Equipment Mounting

a.  The Customer shall provide space and supports for the Company's current and 
	potential transformers as part of the service entrance equipment structure.

b.  The supports shall be drilled for mounting bolts in accordance with dimension 
	information concerning this equipment furnished to the Customer for the design 
	of their installation.

c.  The Customer's station service transformer shall be on the load side of the 
	billing metering transformers.

2.	Secondary Connection Conduit

a.  The Customer shall furnish, install and maintain conduit for the wiring from 
	metering transformers to the billing meter panel.

b.  The conduit shall be at least 1-1/2" galvanized steel or an equivalent approved 
	by the Company.

c.  The conduit shall be run by the shortest practicable route, using conduit bends 
	instead of conduit fittings.

d.  The conduit shall normally not exceed 100 circuit feet and with no more than 
	two 90 degree bends.

e.  This conduit shall be grounded.

f.  A pull wire shall be installed in the completed conduit.

April	2002	22	ESB 752-1994, 2nd Printing

3.	Meter Panel Specification

The Customer shall provide a panel for billing meters, together with mounting for the panel. The panel may be one of the following:

a. 	3/4" thick painted or stained plywood panel, wall mounted, minimum of 48" x

48". For installation of 2000kW and above, a minimum of 48" wide x 60" high panel shall be provided.

(1) The wall-mounted plywood panel shall be located with lower edge 30" from 
	the floor and so that there is a clear working space of not less than 48" from 
	the panel front.

b. 	3/4" minimum thickness Benelex  #70 panel, or other approved insulating

material, switchgear mounted a minimum of 30" wide and 60" high.  The switchgear cubicle must be 36" wide minimum.

(1) The switchgear mounted panel should have offset hinges and a meter 
	projection clearance of at least 16" from the front of the panel and stud 
	projection clearance of at least 10" from the rear of the panel.  This type of 
	panel can only be furnished in an indoor location or walk-in aisle type 
	switchgear.

4.	Meter Panel Location

a.  The billing meter panel should be located indoors in a heated and lighted 
	location conveniently and safely accessible to authorized Company employees.

b.  The location should be clean, dry and free of corrosive atmospheres.

c.  A 20 ampere, 120 volt, single phase convenience receptacle, served from the 
	Customer's distribution panel, shall be installed at the meter panel location.

5. 	For outdoor service equipment installations where a suitable indoor metal panel

location cannot otherwise be provided, the Customer may be required to erect a 
meter house as shown in Figure 8 in the rear of this booklet. This house must be 
provided with heating facilities, one light outlet and one 20 ampere, 120 volt, single

phase convenience receptacle served from the Customer's distribution panel.

6. 	Where the Customer elects to install outdoor metalclad switchgear not of the walk-

in aisle type, the Customer may provide a separate walk-in cubicle, 36" wide minimum, to be used solely for the billing meters.

a.  The billing meters shall be located on a Benelex 	#70, or other approved

insulating material panel furnished and installed on the back wall of the cubicle by the Customer.

b.  The panel shall be in one piece and a minimum of 3/4" thick x 30" wide x 60" 
	high, mounted with the center point 48" above the floor.

c.  The cubicle shall be safely and conveniently accessible to authorized Company 
	employees, clear of all obstructions, clean, dry, free of corrosive atmosphere, 
	heated,  ventilated,  lighted  and  with  a 20  ampere,  120  volt,  single  phase

convenience receptacle, served from the Customer's distribution panel and installed at the meter panel location.

d.  The cubicle shall have a hinged door capable of being opened from the inside of 
	the cubicle.

ESB 752-1994 2nd Printing	23	April 2002

e.  The door shall be locked with a Company padlock.

7. 	At an outdoor substation with a single transformer and where a control building is

not otherwise needed, a weatherproof metal metering cabinet may be acceptable to the Company.

a.  Cabinet dimensions shall normally be 48" x 48" x 18"; larger dimensions may 
	be required for certain applications.

b.  It may be mounted on a column of the metering transformers support structure 
	with its lower edge 30" above finished grade.

c.  The door shall be equipped with a doorstop to secure the door in open position 
	and shall have padlock provision.

d.  A 3/4" painted plywood panel normally 42" x 42" shall be mounted in the rear 
	of the cabinet with 1" clear space between the rear wall and the plywood panel.

e.  A thermostat controlled heater and a 20 ampere, 120 volt, single phase ground 
	fault protected receptacle shall be provided in the panel, to be supplied from the 
	Customer's station service transformer.

f.  Cabinet shall be cross vented top and bottom with filters.

C.	REMOTE METERING

1.	The Company will specify when a telephone conduit and circuit is required to the

metering facilities.

2. 	Where the Customer desires control or metering facilities other than billing metering

located remote from the main substation location, consideration should be given to 
the use of isolating and/or neutralizing transformers in the low voltage circuits from 
substation to the control or meter equipment.  In each case the peculiarities of each 
installation must be specifically studies to determine the advisability of  such 
protective measures.

April 2002	24	ESB 752-1994, 2nd Printing

1.	Safety Clearance to Substation Fences

A.  Dimension "H" is the Minimum Vertical Clearance to Unguarded Live Parts for 
	Vehicular Traffic from Figure 2.

B.  Dimension "D" is the Minimum Vertical Clearance of Unguarded Live Parts for 
	Personnel on Foot from Figure 2.

C.  Dimension "S" is the Safety Clearance determined from Figure 2.

D.  The Safety Clearance boundary is located by constructing an arc with Radius "S" 
	from a point on the centerline of the station fence (without regard to fence height) 
	such that the arc intersects the horizontal line defined by Dimension "D" and is 
	tangent to the horizontal line Defined by Dimension "H" and to the vertical line 
	defined by Dimension "S" measured horizontally from the fence center line.  All 
	exposed live parts shall be outside this Safety Clearance boundary shown above.

2. 	Minimum Vertical Clearance in Areas Accessible to Vehicular Traffic

The vertical clearance is measured vertically from finished crushed stone surface 
to the lowest conductor or live part.  The tabulated clearances are based on 
National Electrical Safety Code clearances for highways, roads, streets and fields 
subject  to  truck  traffic  with  voltage  adder  and  allowance  for  sag  due  to 
temperature.

3. 	Access Clearance to Substation Fences

Normal design practice is to provide adequate drive space between the perimeter 
fence and the structure for maintenance trucks.  However, when the drive space 
cannot be provided, the minimum fence to live part clearance shall not be less 
than the safety Clearance dimension determined by use of sketch shown above.

The intent of these safety clearance requirements is to prevent unqualified or public personnel from coming into accidental contact with live parts by inserting sticks or poles, etc., over or through a fence or wall.

SAFETY CLEARANCE REQUIREMENTS 
	FIGURE 3

April 2002	ESB 752-1994, 2nd Printing

TABLE of INDOOR SEPARATIONS*

Max. kV Class Rating	5.08	8.25	15	25.8	38	38

2400V	6900V	8320V

Nominal System Voltage	4160V	7620V	12kV	23kV	34.5kV	34.5kV

4800V	13.2kV

BIL in kV	60	75	95	125	150	200

Spacing of	Rec.	12"	14"	18"	20"	24"	26”

Buses	Min.	9"	10"	12"	14"	18"	20”

Spacing of

Live Part-to-Live	Min.	4.5"	5.5"	7.5"	13"	14.5"	18”

Part

Spacing of

Live Parts-to-	Min.	3"	4"	5"	8"	10.5"	13”

Ground

Minimum

Clearance To 
	Unguarded 
	Live Parts

Vert.	9'-0"	9'-6"

Horiz.	4’-0"	4’-0"

9'-6"	10'-0"	10'-0"	10'-0"

5’-0"	5’-0"	6’-0"	6’-0"

*Note:  These separations are minimums and should not be considered  recommended  design.   The 
	Company recommends exceeding minimums where space permits.

INDOOR STRUCTURE

ELECTRICAL CLEARANCES

FIGURE 4

ESB 752-1994, 2nd Printing	April 2002

STATION GROUNDING 
	FIGURE 5

April 2002	ESB 752-1994, 2nd Printing

STATION GROUNDING 
FIGURE 5 (CONT’D)

April 2002	ESB 752-1994, 2nd Printing

SWITCH MECHANISM GROUNDING 
	FIGURE 6

ESB 752-1994, 2nd Printing	April 2002

FENCE GROUNDING DETAILS 
	FIGURE 7

April 2002	ESB 752-1994, 2nd Printing

ALTERNATIVE FENCE GROUNDING DETAILS 
	FIGURE 7A

ESB 752-1994, 2nd Printing	April 2002

METER HOUSE 
	FIGURE 8

April 2002	ESB 752-1994, 2nd Printing

SYMBOLS FOR SERVICE EQUIPMENT DIAGRAMS 
	FIGURE 9

ESB 752-1994, 2nd Printing	April 2002

ILLUSTRATION 1

April 2002	ESB 752-1994, 2nd Printing

ILLUSTRATION 2

ESB 752-1994, 2nd Printing	April 2002