Amanda C. Downey

Senior Counsel

April 28, 2017

The Honorable Kimberly D. Bose Secretary

Federal Energy Regulatory Commission 888 First Street, NE

Washington, DC  20426

Re:   New York Independent System Operator, Inc. 
	Docket No. ER11-2402-001

Compliance Filing

Dear Secretary Bose:

Niagara Mohawk Power Corporation (“Niagara Mohawk”) hereby submits its filing to comply with the letter order issued by the Commission in this proceeding on February 10, 2011.1

In the letter order, the Commission conditionally accepted a Large Generator

Interconnection Agreement (“LGIA”) between Niagara Mohawk and WPS Syracuse

Generation, LLC (“WPS Syracuse”),2 subject to Niagara Mohawk’s submittal of a

compliance filing within 30 days after the letter order was issued.  The Commission

directed that in the compliance filing, Niagara Mohawk must either:  (1) revise Appendix 
H to the LGIA with WPS Syracuse to remove Section 5.8 (entitled Information 
Exchange) from the list of sections of the LGIA to which Niagara Mohawk and WPS 
Syracuse believe the NYISO pro forma Large Generator Interconnection Agreement is 
not applicable; or (2) explain why Section 5.8 should continue to be listed in Appendix

H.

Niagara Mohawk regrets the oversight in not submitting this compliance filing

earlier.  Due to an administrative issue that arose when the WPS Syracuse LGIA was

submitted to the Commission, NYISO representatives were listed on the Commission’s e-
mail service list but Niagara Mohawk representatives were not.  NYISO representatives recently pointed out the outstanding compliance obligation to Niagara Mohawk.

1

2

Commission letter order, Docket No. ER11-2402-000 (Feb. 10, 2011). 
The LGIA with WPS Syracuse is designated as Service Agreement No. 316 under the New York

Independent System Operator Inc.’s (“NYISO”) Open Access Transmission Tariff, with an effective date of February 15, 2011.

40 Sylvan Road, Waltham, MA 02451

 T: 781-907-2136  F: 781-296-8092  amanda.downey@nationalgrid.com  www.nationalgrid.com

The Honorable Kimberly D. Bose April 28, 2017

Page 2

In the instant compliance filing, Niagara Mohawk has revised the Appendices to 
the LGIA with WPS Syracuse to remove Section 5.8 from the list of inapplicable 
provisions in Appendix H.  Niagara Mohawk notes that the delay in removing Section 5.8 
from the list did not result in any harm.  Section 5.8 addresses the exchange of design 
information about Attachment Facilities prior to their construction so that the parties can 
work “in good faith to make any necessary design changes.”  No new Attachment 
Facilities associated with the WPS Syracuse facility have been designed or constructed 
since 2011.

The clean version of the revised Appendices to the LGIA with WPS Syracuse is provided in Attachment A hereto, and the revision to Appendix H of the Appendices is shown in red-line format in Attachment B hereto.

Please contact the undersigned with any questions.  Thank you.

Respectfully submitted,

/s/ Amanda C. Downey

Amanda C. Downey 
Senior Counsel

National Grid USA

Service Company, Inc.

40 Sylvan Road

Waltham, MA 02451

Attorney for Niagara Mohawk Power Corporation

CERTIFICATE OF SERVICE

I hereby certify that I have this day caused the foregoing document to be served 
upon each person designated on the official service list compiled by the Secretary in this 
proceeding.

Dated at Washington, DC, this 28th day of April, 2017.

/s/ Daniel Klein

Daniel Klein

Alston & Bird LLP

Attachment A

Appendix A

Appendix B

Milestones

Appendix C

Interconnection Details

1. Owner:

Project:

Point of Interconnection: (refer to one-line diagram that should be attached in Appendix A)

2.  Electrical Equipment Requirements: The installation of electrical equipment and operation 
	of the facility must meet or exceed the requirements of Niagara Mohawk's Electric System 
	Bulletin No.ESB 756.

3.  Metering Requirements: Electricity transferred to the transmission system shall be measured 
	by electric watt-hour meters of a type approved by the Public Service Commission of the State 
	of New York. The meter and installation costs shall be borne by WPS Syracuse Generation 
	LLC. The meters shall be maintained with the rules set forth in 16 NYCRR Part 92.

4.  Reference:

5.  Reference:

Appendix D

Security Arrangements Details

Infrastructure security of New York State Transmission System equipment and operations and control hardware and software is essential to ensure day-to-day New York State Transmission System reliability and operational security. The Commission will expect the NYISO, all Transmission Owners, all Developers and all other Market Participants to comply with the recommendations 
offered by the President's Critical Infrastructure Protection Board and, eventually, best practice 
recommendations from the electric reliability authority. All public utilities will be expected to 
meet basic standards for system infrastructure and operational security, including physical, 
operational, and cyber-security practices.

Appendix E

Commercial Operation Date

For purposes of this Agreement, the Commercial Operation Date shall be treated as 10/20/92.

Appendix F

Addresses for Delivery of Notices and Billings Notices:

NYISO:

New York Independent System Operator Attn: Vice President, Operations

3890 Carman Rd.

Schenectady, NY 12303

Transmission Owner:

Vice President , Transmission Commercial Services National Grid

40 Sylvan Road

Waltham, MA 02451 
Phone: (781) 907-5706

Email: mary.ellen.paravalos@us.ngrid.corn

Developer:

Contract Administration

WPS Syracuse Generation, LLC 1716 Lawrence Drive

DePere, WI 54115

Billings and Payments:

Transmission Owner:

Vice President , Transmission Commercial Services National Grid

40 Sylvan Road

Waltham, MA 02451 
Phone: (781) 907-5706

Email: mary.ellen.paravalos@us.ngrid.com

Developer:

Contract Administration

WPS Syracuse Generation, LLC 1716 Lawrence Drive

DePere, WI 54115

Alternative Forms of Delivery of Notices (telephone, facsimile or email): NYISO:

New York Independent System Operator Attn: Vice President, Operations

3890 Carman Rd.

Schenectady, NY 12303

Transmission Owner:

Vice President Transmission Commercial Services National Grid

40 Sylvan Road

Waltham, MA 02451 
Phone: (781) 907-2422

Email: mary.ellen.paravalos@us.ngrid.com

Developer:

Contract Administration

WPS Syracuse Generation, LLC 1716 Lawrence Drive DePere, WI 54115

APPENDIX G

INTERCONNECTION REQUIREMENTS FOR A WIND GENERATING PLANT

Appendix G sets forth requirements and provisions specific to a wind generating plant. 
All other requirements of this LG1A continue to apply to wind generating plant interconnections.

A. 	Technical Standards Applicable to a Wind Generating Plant

Low Voltage Ride-Through (LVRT) Capability

A wind generating plant shall be able to remain online during voltage disturbances up to the time periods and associated voltage levels set forth in the standard below. The LVRT standard provides for a transition period standard and a post-transition period standard.

Transition Period LVRT Standard

The transition period standard applies to wind generating plants subject to FERC Order 661 
that have either: (i) interconnection agreements signed and filed with the Commission, filed with the 
Commission in unexecuted form, finally executed as conforming agreements, or filed with the 
Commission as non-conforming agreements between January 1, 2006 and December 31, 2006, with a 
scheduled in-service date no later than December 31, 2007, or (ii) wind generating turbines subject 
to a wind turbine procurement contract executed prior to December 31, 2005, for delivery through 
2007.

1. 	Wind generating plants are required to remain in-service during three-phase faults with

normal clearing (which is a time period of approximately 4 - 9 cycles) and single line to

ground faults with delayed clearing, and subsequent post-fault voltage recovery to prefault 
voltage unless clearing the fault effectively disconnects the generator from the system. The 
clearing time requirement for a three-phase fault will be specific to the wind generating 
plant substation location, as determined by and documented by the Transmission Owner for 
the Transmission District to which the wind generating plant will be interconnected. The 
maximum clearing time the wind generating plant shall be required to withstand for a

three-phase fault shall be 9 cycles at a voltage as low as 0.15 p.u., as measured at the high

side of the wind generating plant step-up transformer (i.e. the transformer that steps the

voltage up to the transmission interconnection voltage or "GSU"), after which, if the fault

remains following the location-specific normal clearing time for three-phase faults, the wind generating plant may disconnect from the transmission system.

2. 	This requirement does not apply to faults that would occur between the wind generator terminals

and the high side of the GSU or to faults that would result in a voltage lower than 0.15 per unit on the high side of the GSU serving the facility.

3.	Wind generating plants may be tripped after the fault period if this action is intended as part of

a special protection system.

4. 	Wind generating plants may meet the LVRT requirements of this standard by the performance

of the generators or by installing additional equipment (e.g., Static VAr Compensator, etc.)

within the wind generating plant or by a combination of generator performance and additional equipment.

5. 	Existing individual generator units that are, or have been, interconnected to the network at the

same location at the effective date of the Appendix G LVRT Standard are exempt from meeting 
the Appendix G LVRT Standard for the remaining life of the existing generation equipment. 
Existing individual generator units that are replaced are required to meet the Appendix G 
LVRT Standard.

Post-transition Period LVRT Standard

All wind generating plants subject to FERC Order No. 661 and not covered by the transition period described above must meet the following requirements:

1. 	Wind generating plants are required to remain in-service during three-phase faults with

normal clearing (which is a time period of approximately 4 - 9 cycles) and single line to 
ground faults with delayed clearing, and subsequent post-fault voltage recovery to prefault 
voltage unless clearing the fault effectively disconnects the generator from the system. The 
clearing time requirement for a three-phase fault will be specific to the wind generating plant 
substation location, as determined by and documented by the Transmission Owner for the 
Transmission District to which the wind generating plant will be interconnected. The

maximum clearing time the wind generating plant shall be required to withstand for a

three-phase fault shall be 9 cycles after which, if the fault remains following the

location-specific normal clearing time for three-phase faults, the wind generating plant may disconnect from the transmission system. A wind generating plant shall remain 
interconnected during such a fault on the transmission system for a voltage level as low as zero volts, as measured at the high voltage side of the wind GSU.

2.	This requirement does not apply to faults that would occur between the wind generator terminals

and the high side of the GSU.

3.	Wind generating plants may be tripped after the fault period if this action is intended as part of a

special protection system.

4. 	Wind generating plants may meet the LVRT requirements of this standard by the performance

of the generators or by installing additional equipment (e.g., Static VAr Compensator) within the 
wind generating plant or by a combination of generator performance and additional equipment.

5. 	Existing individual generator units that are, or have been, interconnected to the network at the

same location at the effective date of the Appendix G LVRT Standard are exempt from meeting 
the Appendix G LVRT Standard for the remaining life of the existing generation equipment. 
Existing individual generator units that are replaced are required to meet the Appendix G 
LVRT Standard.

i.i	Power Factor Design Criteria (Reactive Power)

A wind generating plant shall maintain a power factor within the range of 0.95 leading to

0.95 lagging, measured at the Point of Interconnection as defined in this LGIA, if the ISO's System

Reliability Impact Study shows that such a requirement is necessary to ensure safety or reliability.

The power factor range standards can be met using, for example without limitation, power

electronics designed to supply this level of reactive capability (taking into account any limitations 
due to voltage level, real power output, etc.) or fixed and switched capacitors if agreed to by the 
Transmission Owner for the Transmission District to which the wind generating plant will be 
interconnected, or a combination of the two. The Developer shall not disable power factor equipment 
while the wind plant is in operation. Wind plants shall also be able to provide sufficient dynamic

voltage support in lieu of the power system stabilizer and automatic voltage regulation at the generator excitation system if the System Reliability Impact Study shows this to be required for system safety or reliability.

iii. 	Supervisory Control and Data Acquisition (SCADA) Capability

The wind plant shall provide SCADA capability to transmit data and receive instructions from 
the ISO and/or the Transmission Owner for the Transmission District to which the wind generating 
plant will be interconnected, as applicable, to protect system reliability. The Transmission Owner 
for the Transmission District to which the wind generating plant will be interconnected and the wind 
plant Developer shall determine what SCADA information is essential for the proposed wind plant, 
taking into account the size of the plant and its characteristics, location, and importance in

maintaining generation resource adequacy and transmission system reliability in its area.

Appendix H

List of Non-Applicable Pro-Forma LGIA Provisions

Transmission Owner and Developer are already interconnected, pursuant to a pre-existing

interconnection agreement. Therefore, certain terms of the pro-forma New York ISO LGIA are not applicable to this LGIA, because they relate solely to new interconnections. The parties to this LGIA have nevertheless agreed to use the pro-forma New York ISO LGIA with almost no modifications, in accordance with FERC policy promoting the use of pro-forma interconnection agreements wherever possible. The parties, however, believe that the following provisions of the pro-forma New York ISO LGIA are not applicable to the current LG IA:

Section 5.1 (Option), including all subsections thereof

Section 5.2 (General Conditions Applicable to Option to Build) Section 5.3 (Liquidated Damages)

Section 5.5 (Equipment Procurement), including all subsections thereof

Section 5.6 (Construction Commencement), including all subsections thereof Section 5.7 (Work Progress)

Section 5.9 (Limited Operation)

Section 5.10 (Developer Attachment Facilities), including all subsections thereof

Section 5.11 (Transmission Owner Attachment Facilities), including all subsections thereof Section 5.14 (Permits)

Section 5.15 (Early Construction of Base Case Facilities)

Section 6.1 (Pre Commercial Operation Date Testing and Modification)

Section 11.4 (Special Provisions for Affected Systems)

Section 11.5 (Provision of Security), including all subsections thereof

Section 12.2 (Final Invoice)

Section 24.1 (Information Acquisition)

Section 24.2 (Information Submission by Transmission Owner) Section 24.3 (Updated Information Submission by Developer) Section 24.4 (Information Supplementation)

Section 25.4.1 (Audit Rights Period for Construction Related Accounts)

Appendix B (Milestones)

Appendix G (Interconnection Requirements for a Wind Generating Plant)

Attachment B

Appendix A

Appendix B

Milestones

Appendix C

Interconnection Details

1. Owner:

Project:

Point of Interconnection: (refer to one-line diagram that should be attached in Appendix A)

2.  Electrical Equipment Requirements: The installation of electrical equipment and

operation of the facility must meet or exceed the requirements of Niagara Mohawk's Electric System Bulletin No.ESB 756.

3.  Metering Requirements: Electricity transferred to the transmission system shall be

measured by electric watt-hour meters of a type approved by the Public Service Commission 
of the State of New York. The meter and installation costs shall be borne by WPS Syracuse 
Generation LLC. The meters shall be maintained with the rules set forth in 16 NYCRR Part

92.

4.  Reference:

5.  Reference:

Appendix D

Security Arrangements Details

Infrastructure security of New York State Transmission System equipment and operations and control hardware and software is essential to ensure day-to-day New York State Transmission System reliability and operational security. The Commission will expect the NYISO, all 
Transmission Owners, all Developers and all other Market Participants to comply with the 
recommendations offered by the President's Critical Infrastructure Protection Board and, 
eventually, best practice recommendations from the electric reliability authority. All public 
utilities will be expected to meet basic standards for system infrastructure and operational security, including physical, operational, and cyber-security practices.

Appendix E

Commercial Operation Date

For purposes of this Agreement, the Commercial Operation Date shall be treated as 10/20/92.

Appendix F

Addresses for Delivery of Notices and Billings Notices:

NYISO:

New York Independent System Operator Attn: Vice President, Operations

3890 Carman Rd.

Schenectady, NY 12303

Transmission Owner:

Vice President , Transmission Commercial Services National Grid

40 Sylvan Road

Waltham, MA 02451 
Phone: (781) 907-5706

Email: mary.ellen.paravalos@us.ngrid.corn

Developer:

Contract Administration

WPS Syracuse Generation, LLC 1716 Lawrence Drive

DePere, WI 54115

Billings and Payments:

Transmission Owner:

Vice President , Transmission Commercial Services National Grid

40 Sylvan Road

Waltham, MA 02451 
Phone: (781) 907-5706

Email: mary.ellen.paravalos@us.ngrid.com

Developer:

Contract Administration

WPS Syracuse Generation, LLC 1716 Lawrence Drive

DePere, WI 54115

Alternative Forms of Delivery of Notices (telephone, facsimile or email): NYISO:

New York Independent System Operator Attn: Vice President, Operations

3890 Carman Rd.

Schenectady, NY 12303

Transmission Owner:

Vice President Transmission Commercial Services National Grid

40 Sylvan Road

Waltham, MA 02451 
Phone: (781) 907-2422

Email: mary.ellen.paravalos@us.ngrid.com

Developer:

Contract Administration

WPS Syracuse Generation, LLC 1716 Lawrence Drive DePere, WI 54115

APPENDIX G

INTERCONNECTION REQUIREMENTS FOR A WIND GENERATING PLANT

Appendix G sets forth requirements and provisions specific to a wind generating plant. 
All other requirements of this LG1A continue to apply to wind generating plant interconnections.

A. 	Technical Standards Applicable to a Wind Generating Plant

Low Voltage Ride-Through (LVRT) Capability

A wind generating plant shall be able to remain online during voltage disturbances up to the time periods and associated voltage levels set forth in the standard below. The LVRT standard provides for a transition period standard and a post-transition period standard.

Transition Period LVRT Standard

The transition period standard applies to wind generating plants subject to FERC Order 
661 that have either: (i) interconnection agreements signed and filed with the Commission, filed with 
the Commission in unexecuted form, finally executed as conforming agreements, or filed with the 
Commission as non-conforming agreements between January 1, 2006 and December 31, 2006, with a 
scheduled in-service date no later than December 31, 2007, or (ii) wind generating turbines 
subject to a wind turbine procurement contract executed prior to December 31, 2005, for delivery 
through 2007.

1. 	Wind generating plants are required to remain in-service during three-phase faults with

normal clearing (which is a time period of approximately 4 - 9 cycles) and single line to 
ground faults with delayed clearing, and subsequent post-fault voltage recovery to 
prefault voltage unless clearing the fault effectively disconnects the generator from the 
system. The clearing time requirement for a three-phase fault will be specific to the wind 
generating plant substation location, as determined by and documented by the 
Transmission Owner for the Transmission District to which the wind generating plant will 
be interconnected. The maximum clearing time the wind generating plant shall be required 
to withstand for a three-phase fault shall be 9 cycles at a voltage as low as 0.15 p.u., as

measured at the high side of the wind generating plant step-up transformer (i.e. the

transformer that steps the voltage up to the transmission interconnection voltage or "GSU"), 
after which, if the fault remains following the location-specific normal clearing time for 
three-phase faults, the wind generating plant may disconnect from the transmission system.

2. 	This requirement does not apply to faults that would occur between the wind generator terminals

and the high side of the GSU or to faults that would result in a voltage lower than 0.15 per unit on the high side of the GSU serving the facility.

3.	Wind generating plants may be tripped after the fault period if this action is intended as part

of a special protection system.

4. 	Wind generating plants may meet the LVRT requirements of this standard by the performance

of the generators or by installing additional equipment (e.g., Static VAr Compensator, etc.)

within the wind generating plant or by a combination of generator performance and additional equipment.

5. 	Existing individual generator units that are, or have been, interconnected to the network at the

same location at the effective date of the Appendix G LVRT Standard are exempt from meeting 
the Appendix G LVRT Standard for the remaining life of the existing generation equipment. 
Existing individual generator units that are replaced are required to meet the Appendix G 
LVRT Standard.

Post-transition Period LVRT Standard

All wind generating plants subject to FERC Order No. 661 and not covered by the transition period described above must meet the following requirements:

1. 	Wind generating plants are required to remain in-service during three-phase faults with

normal clearing (which is a time period of approximately 4 - 9 cycles) and single line to 
ground faults with delayed clearing, and subsequent post-fault voltage recovery to prefault 
voltage unless clearing the fault effectively disconnects the generator from the system. The 
clearing time requirement for a three-phase fault will be specific to the wind generating plant 
substation location, as determined by and documented by the Transmission Owner for the 
Transmission District to which the wind generating plant will be interconnected. The

maximum clearing time the wind generating plant shall be required to withstand for a threephase fault shall be 9 cycles after which, if the fault remains following the location-specific normal clearing time for three-phase faults, the wind generating plant may disconnect from the transmission system. A wind generating plant shall remain interconnected during such a fault on the transmission system for a voltage level as low as zero volts, as measured at the high voltage side of the wind GSU.

2.	This requirement does not apply to faults that would occur between the wind generator terminals

and the high side of the GSU.

3.	Wind generating plants may be tripped after the fault period if this action is intended as part of

a special protection system.

4. 	Wind generating plants may meet the LVRT requirements of this standard by the

performance of the generators or by installing additional equipment (e.g., Static VAr

Compensator) within the wind generating plant or by a combination of generator performance and additional equipment.

5. 	Existing individual generator units that are, or have been, interconnected to the network at the

same location at the effective date of the Appendix G LVRT Standard are exempt from

meeting the Appendix G LVRT Standard for the remaining life of the existing generation equipment.  Existing individual generator units that are replaced are required to meet the Appendix G LVRT Standard.

i.i	Power Factor Design Criteria (Reactive Power)

A wind generating plant shall maintain a power factor within the range of 0.95 leading to

0.95 lagging, measured at the Point of Interconnection as defined in this LGIA, if the ISO's System

Reliability Impact Study shows that such a requirement is necessary to ensure safety or reliability.

The power factor range standards can be met using, for example without limitation, power 
electronics designed to supply this level of reactive capability (taking into account any 
limitations due to voltage level, real power output, etc.) or fixed and switched capacitors if agreed 
to by the Transmission Owner for the Transmission District to which the wind generating plant 
will be interconnected, or a combination of the two. The Developer shall not disable power factor

equipment while the wind plant is in operation. Wind plants shall also be able to provide

sufficient dynamic voltage support in lieu of the power system stabilizer and automatic voltage regulation at the generator excitation system if the System Reliability Impact Study shows this to be required for system safety or reliability.

iii. 	Supervisory Control and Data Acquisition (SCADA) Capability

The wind plant shall provide SCADA capability to transmit data and receive instructions from the ISO and/or the Transmission Owner for the Transmission District to which the wind 
generating plant will be interconnected, as applicable, to protect system reliability. The 
Transmission Owner for the Transmission District to which the wind generating plant will be 
interconnected and the wind plant Developer shall determine what SCADA information is 
essential for the proposed wind plant, taking into account the size of the plant and its 
characteristics, location, and importance in maintaining generation resource adequacy and 
transmission system reliability in its area.

Appendix H

List of Non-Applicable Pro-Forma LGIA Provisions

Transmission Owner and Developer are already interconnected, pursuant to a pre-existing

interconnection agreement. Therefore, certain terms of the pro-forma New York ISO LGIA are not applicable to this LGIA, because they relate solely to new interconnections. The parties to this LGIA have nevertheless agreed to use the pro-forma New York ISO LGIA with almost no modifications, in accordance with FERC policy promoting the use of pro-forma interconnection agreements wherever possible. The parties, however, believe that the following provisions of the pro-forma New York ISO LGIA are not applicable to the current LG IA:

Section 5.1 (Option), including all subsections thereof

Section 5.2 (General Conditions Applicable to Option to Build) Section 5.3 (Liquidated Damages)

Section 5.5 (Equipment Procurement), including all subsections thereof

Section 5.6 (Construction Commencement), including all subsections thereof Section 5.7 (Work Progress)

Section 5.8 (Information Exchange)

Section 5.9 (Limited Operation)

Section 5.10 (Developer Attachment Facilities), including all subsections thereof

Section 5.11 (Transmission Owner Attachment Facilities), including all subsections thereof Section 5.14 (Permits)

Section 5.15 (Early Construction of Base Case Facilities)

Section 6.1 (Pre Commercial Operation Date Testing and Modification)

Section 11.4 (Special Provisions for Affected Systems)

Section 11.5 (Provision of Security), including all subsections thereof

Section 12.2 (Final Invoice)

Section 24.1 (Information Acquisition)

Section 24.2 (Information Submission by Transmission Owner) Section 24.3 (Updated Information Submission by Developer) Section 24.4 (Information Supplementation)

Section 25.4.1 (Audit Rights Period for Construction Related Accounts)

Appendix B (Milestones)

Appendix G (Interconnection Requirements for a Wind Generating Plant)