November 7, 2019

Hon. Kimberly Bose Secretary

Federal Energy Regulatory Commission 888 First Street, N.E.

Washington, D.C.  20426

Re:    New York Independent System Operator, Inc., Notification of Major Emergency 
	in the New York Control Area; Docket No. EY20-__-000

Dear Secretary Bose:

Pursuant to Section 2.13 of its Open Access Transmission Tariff (“OATT”), the New York 
Independent System Operator, Inc. (“NYISO”) hereby notifies the Commission that an “Emergency 
State” existed in the New York Control Area on November 7, 2019 at 00:04.  As a result, the NYISO 
was required to take special action to ensure that the reliability of the New York State Transmission 
System was not adversely affected.  The NYISO has enclosed documentation describing the 
Emergency State and its actions.  As required by Section 2.13 of the OATT, the NYISO has also 
notified the New York State Public Service Commission of the Emergency State and its actions.

Please feel free to contact me at (518) 356-6159 if you have any questions or comments. 
	Sincerely,

/s/ Gregory Campoli

Gregory Campoli

Manager, Reliability, Compliance & Industry Affairs New York Independent System Operator

Enclosure

Cc:  Wes Yeomans 
	Ray Stalter

Chris Sharp

10 Krey Boulevard, Rensselaer, New York 12144 | www.nyiso.com

NYISO Major Emergency Report

At 0004 on 11/07/2019  a Major Emergency was declared by the NYISO Shift Supervisor

when the power flow on Central East VC

exceeded its Voltage Transfer Limit by more than 105%

This was caused by: 	Energy flows into ISO-NE exceeded scheduled amounts.

To correct this the

NYISO Shift	Requested ISO-NE reduce flows to scheduled amounts, moved Phase

Supervisor:	Angle Regulators (PARs) to reduce flows and placed a capacitor in

service to increase the limit.

Load relief was not required.

The Major Emergency was terminated at 0006 on 11/07/2019