UNITED STATES OF AMERICA 
	BEFORE THE

FEDERAL ENERGY REGULATORY COMMISSION

Reactive Power Requirements	)

for Non-Synchronous Generation	)	Docket No. RM16-1

___________________	)

Comments of the ISO/RTO Council

The ISO/RTO Council submits comments on the proposal of the Federal Energy 
Regulatory Commission to revise standard generator interconnection agreements to 
eliminate the exemptions for wind generators from the requirement to provide reactive 
power.1  If adopted, the Commission’s proposal would require all newly interconnecting 
generators that are subject to the interconnection procedures of an independent system 
operator (ISO) or regional transmission provider (RTO), including both synchronous and 
non-synchronous generators, to provide dynamic reactive power capability to the 
electricity grid.  This proposal eliminates unduly discriminatory treatment as between 
synchronous and non-synchronous resources with respect to the requirement to provide 
reactive power capability.  Technology enhancements, as well as the relatively modest 
incremental cost to non-synchronous resources of providing reactive power capability, 
support the Commission’s proposal as just and reasonable. For these reasons, the 
ISO/RTO Council urges the Commission to adopt its proposal as soon as possible.

1

Reactive Power Requirements for Non-Synchronous Generation, Proposal to Revise Standard

Generator Interconnection Agreements (Proposal); RM16-1 (2015).

The ISO/RTO Council includes the Alberta Electric System Operator (AESO), the California 
Independent System Operator Corporation (CAISO), the Electric Reliability Council of Texas, Inc., 
(ERCOT) the Independent Electricity System Operator (IESO), ISO New England, Inc., (ISO-NE), the 
Midcontinent Independent System Operator, Inc. (MISO), the New York Independent System Operator, 
Inc. (NYISO), PJM Interconnection, L.L.C., (PJM) and the Southwest Power Pool (SPP).  ERCOT, AESO 
and IESO are not subject to the Commission’s jurisdiction and are not joining these comments.

1

I.	Background

Since the adoption of Order 661 and Order 661-A, transmission providers have 
had to undertake time-consuming interconnection studies to assess whether a wind 
resource needs to provide reactive power capability in order to safely and reliably 
interconnect to the grid.2  Last year, the Commission approved tariff revisions submitted by PJM Interconnection that require that all non-synchronous resources, including wind resources, seeking to interconnect to the grid use enhanced inverters and provide 
reactive power capability without requiring PJM to demonstrate the need for this 
capability in the interconnection study process.3  Other jurisdictions in North America 
have also established requirements for non-synchronous resources to provide reactive power capability as a condition of interconnection.4  Last month, the Essential Reliability Services Task Force of the North American Electric Reliability Corporation (NERC) 
determined that all new resources need to provide sufficient voltage control as an 
essential component of a reliable Bulk Power System.5

2

Interconnection for Wind Energy, Order No. 661, FERC Stats. & Regs. ¶ 31,186, at P 51, order

on reh’g, Order No. 661-A, FERC Stats. & Regs. ¶ 31,198 (2005).

3

PJM Interconnection LLC, 151 FERC ¶ 61,097 (2015)

http://www.ferc.gov/CalendarFiles/20150505165917-ER15-1193-000.pdf

4

For example, Electric Reliability Council of Texas, Inc. (ERCOT), a region that has well in excess

of 14 GW of installed non-synchronous capacity, has had for years a uniform reactive power requirement 
that applies to all generation resources.  See Protocol Section 3.15, Voltage Support. 
http://www.ercot.com/mktrules/nprotocols/current.

See also, April 17, 2012 FERC Technical Conference on Reactive Power Resources (AD12-10-
000), Transcript at 120:18-121:13.  http://www.ferc.gov/CalendarFiles/20120426074709-AD12-10-04-17-

12.pdf

5

See Abstract of NERC Essential Reliability Task Force Measures Framework Report dated

December 2015:

http://www.nerc.com/comm/Other/essntlrlbltysrvcstskfrcDL/ERS%20Abstract%20Report%20Final.pdf

2

The Commission is proposing to modify its pro forma large generator

interconnection agreement and pro forma small generator interconnection agreement to 
eliminate the current exemption for wind generators from the requirement to provide 
reactive power.  As a result, all new generators seeking to interconnect to the 
transmission system and all existing non-synchronous generators making upgrades to 
their generation facilities that require new interconnection requests will need to provide 
reactive power capability.  The Commission proposes that these resources design their 
generating facilities to maintain a composite power delivery at continuous rated power 
output at the point of interconnection at a power factor of 0.95 leading to 0.95 lagging, 
or a different range if adopted by the transmission provider.  Similar to reactive power 
provided by synchronous resources, the Commission proposes that reactive power 
capability installed by non-synchronous generators must be dynamic.  The Commission 
also proposes to require that non-synchronous generators maintain the required power 
factor range only when the generator’s real power output exceeds 10 percent of its 
nameplate capacity.

The ISO/RTO Council generally supports the Commission’s proposed technical 
specifications, but requests that the Commission recognize appropriate independent 
entity variations and regional differences as part of compliance with a final order in this 
proceeding.  For example, each ISO and RTO in the ISO/RTO Council does not 
uniformly agree that non-synchronous resources should maintain the required power 
factor range only when the generator’s real power output exceeds 10 percent of its 
nameplate capacity.  Instead, each ISO and RTO believes non-synchronous resources 
should provide reactive power capability in a manner comparable to synchronous

3

resources, with each ISO/RTO able to establish rules on a showing that their individual situation merits.

II. 	The Commission’s proposal treats synchronous and non-synchronous

resources in a comparable manner for purposes of reactive power.

As the number and size of non-synchronous resources increases, the

Commission is appropriately proposing to require that all resources interconnecting to 
the transmission system provide reactive power capability.  By extending this 
requirement to non-synchronous resources as a condition of interconnection - for those 
generators subject to an ISO’s or RTO’s interconnection process - the Commission is 
treating non-synchronous resources in a manner that is comparable to synchronous 
resources.

The disparate treatment of wind resources under Order 661 and Order 661-A as 
compared to synchronous resources may constitute undue discrimination among 
resource types and can create operational challenges.6  Non-synchronous resources 
use inverters to convert non-synchronized power into synchronized alternating current 
power that can flow on the transmission system.  The ISO/RTO Council understands 
that current manufacturers routinely include reactive power capability in standard 
inverters used by non-synchronous resources, thereby making the cost of reactive 
power capability minimal.7  As such, there is no technical reason why non-synchronous 
resources should not provide this capability in a manner comparable to synchronous

6

Absent maintaining sufficient voltages, non-synchronous resources may face operational issues.

See e.g. Bonneville Power Administration description of wind facilities having to operate at lower than optimal levels until they could provide voltage control even though Bonneville’s interconnection studies did not detect voltage issues.  April 17, 2012 FERC Technical Conference on Reactive Power Resources (AD12-10-000), Transcript at 150:24-152:16.

7

See e.g. Comments of Siemens. April 17, 2012 FERC Technical Conference on Reactive Power

Resources (AD12-10-000), Transcript at 119:21-121:13.

4

resources.  By requiring non-synchronous resources to provide reactive power

capability as a condition of interconnection, the Commission can cure this unduly disparate treatment.

Operation and planning of the electric grid requires an adequate level of voltage 
support, which is provided by the generation and transmission that make up the grid. 
The most efficient and effective means of ensuring there is adequate voltage support 
from an operations and planning perspective is to require that all generators subject to 
the interconnection procedures of an ISO or RTO provide dynamic reactive power 
capability.  This establishes a known and consistent baseline of capability to support 
system voltage needs.  Transmission planners can then remedy any deficiencies 
through transmission infrastructure that provides voltage support.  This approach is far 
more effective than trying to tailor voltage requirements of specific resources (in this 
case intermittent resources) relative to a grid that changes all the time.  Trying to 
determine the voltage requirements of a non-synchronous resources through an 
interconnection study specific to a point in time may not reflect reality relative to a 
changing grid and creates the potential for voltage deficiencies.  Transmission planners 
must remedy these deficiencies and they can result in shifting the cost to other entities 
(e.g. load paying for transmission equipment).  Alternatively, establishing a known 
voltage baseline for all resources to provide reactive power capacity mitigates this risk 
and supports effective and efficient system operations and planning.

5

III.	The cost of providing reactive power capability is not a significant

percentage of overall project development costs for non-synchronous resources.

The cost of including reactive power capability as a percentage of total project 
costs is relatively small.8  The ISO/RTO Council recognizes that some entities may 
contest this fact and argue that applying a uniform reactive power requirement to non-
synchronous resources creates significant capital cost.9  While the Commission’s 
proposed uniform requirement for asynchronous resources to provide dynamic reactive 
power capability could impose higher inverter costs on those projects that would 
otherwise avoid such requirements through the system impact study approach, these 
costs are not significant capital costs.  Inverter manufacturers have informed ISO/RTO 
Council members that a small percentage of total plant cost is attributable to inverters 
and associated equipment. This is a required cost because non-synchronous resources 
must use inverters to transfer synchronous power onto the electricity grid.  As 
referenced above, reactive power capability is now a standard feature of inverters used 
in both wind and solar photovoltaic applications at the transmission system level.  There 
is, therefore, no significant additional cost for reactive power capability.  At most, 
developers may need to size their inverters appropriately to ensure they can provide 
reactive power capability as well as real power output they have committed to provide.

8

9

Id. at 141:10-124:6. 
See e.g. Comments of the American Wind Energy Association in response to the April 22, 2014

workshop on Third Party Provision of Reactive Supply and Voltage Control and Regulation and Frequency Response Services filed in FERC Docket AD 14-7 at 7-8.

http://elibrary.ferc.gov/idmws/common/opennat.asp?fileID=13567273

6

IV.	Non-synchronous resources should receive compensation comparable to

synchronous resources for reactive power capability for the provision/absorption of reactive power.

As part of its proposal, the Commission states that non-synchronous generators would be eligible for the same payments for reactive power as other generators and any compensation would be based on the cost of providing reactive power.10  The 
Commission seeks comment on whether the existing methods used to determine 
reactive power compensation are appropriate for wind generators and, if not, what 
alternatives would be appropriate.11

The Commission should adopt an approach that takes into account that various

approaches to compensate resources for reactive power capability exist in different 
ISO/RTO regions.12  In this respect, the Commission should not adopt a uniform 
approach to compensating synchronous or non-synchronous resources for reactive 
power capability or the provision/absorption of reactive power in this proceeding.  Nor 
should the Commission direct transmission providers to modify their compensation 
structures except as necessary to recognize new resource types as eligible to receive 
compensation for leading and lagging reactive power that they are capable of supplying 
to the grid.  To this end, the Commission should allow synchronous and non-
synchronous resources to receive comparable compensation, provided they are 
providing comparable services.  To the extent it is necessary to modify compensation 
approaches for synchronous and non-synchronous facilities providing reactive power

10

11

12

Proposal at P 12. Id. at P 18.

See generally Commission Staff Report, Payment for Reactive Power issued inAD14-7 date April

22, 2014 http://www.ferc.gov/legal/staff-reports/2014/04-11-14-reactive-power.pdf

7

capability, the Commission should allow transmission providers the opportunity to fashion any necessary revisions to their compensation rules on compliance.

V.	Conclusion

The Commission should adopt its proposal to require all newly interconnecting 
generators that are subject to an ISO’s or RTO’s interconnection procedures, including 
both synchronous and non-synchronous generators, to provide reactive power 
capability to the electricity grid.  The proposal eliminates unnecessary disparate 
treatment among resource types.  Technology enhancements as well as the relatively 
modest incremental cost to non-synchronous resources of providing reactive power 
capability support the Commission’s proposal as just and reasonable.  The ISO/RTO 
Council generally supports the Commission’s proposed technical specifications, but 
requests that the Commission recognize appropriate independent entity variations and 
regional differences as part of compliance with a final order in this proceeding.

Respectfully submitted,

/s/ Anna McKenna 
Roger E. Collanton,

General Counsel 
Anna A. McKenna,*

Assistant General Counsel,

California Independent System Operator Corporation

250 Outcropping Way 
Folsom, California 95630

amckenna@caiso.com

/s/ Sara B. Keegan

Robert E. Fernandez, General Counsel

Raymond Stalter,

Director of Regulatory Affairs Carl F. Patka,*

Assistant General Counsel Sara B. Keegan,*

Senior Attorney

New York Independent System Operator, Inc.

10 Krey Boulevard 
Rensselaer, NY 12144

cpatka@nyiso.com

8

/s/ Theodore J. Paradise

Raymond W. Hepper,

Vice President, General Counsel, and Secretary

Theodore J. Paradise,*

Assistant General Counsel, Operations and Planning

ISO New England Inc.

One Sullivan Road

Holyoke, Massachusetts 01040

tparadise@iso-ne.com

/s/ Stephen G. Kozey

Stephen G. Kozey,*

Vice President, General Counsel, and Secretary

J. Matt Harnish,*

Senior Corporate Counsel

Midcontinent Independent System Operator, Inc.

P.O. Box 4202

Carmel, Indiana 46082-4202

skozey@midwestiso.org

*Designated to receive service

Dated: January 27, 2016

/s/ Craig Glazer

Craig Glazer,*

Vice President-Federal Government Policy

Robert V. Eckenrod,* Senior Counsel

PJM Interconnection, L.L.C.

Suite 600

1200 G Street, N.W. Washington, D.C. 20005 202-423-4743

Craig.Glazer@pjm.com

Robert.Eckenrod@pjm.com

/s/ Paul Suskie

Paul Suskie,*

Sr. VP Regulatory Policy & General Counsel

Mike Riley,

Assoc. General Counsel

Southwest Power Pool, Inc.

201 Worthen Drive

Little Rock, Arkansas 72223-4936

psuskie@spp.org

9

CERTIFICATE OF SERVICE

I hereby certify that I have served the foregoing document upon the

parties listed on the official service lists in the above-referenced proceedings, in accordance with the requirements of Rule 2010 of the Commission’s Rules of Practice and Procedure (18 C.F.R. § 385.2010).

Dated at Folsom, California this 27th day of January 2016.

/s/ Anna Pascuzzo

Anna Pascuzzo