FERC rendition of the electronically filed tariff records in Docket No.  ER13-762-

Filing Data:

CID: C000038

Filing Title: Correction to Reimbursement Agreement No. 1949 between Nat'l Grid and Edge Corp. Company Filing Identifier: 654

Type of Filing Code:  130

Associated Filing Identifier: 556 
Tariff Title: NYISO Agreements 
Tariff ID: 58

Payment Confirmation: N 
Suspension Motion:

Tariff Record Data:

Record Content Description: Agreement No. 1949

Tariff Record Title: SA No. 1949 NiMo and EDGE Corp. re: reimbursement costs Record Version Number: 0.1.0

Option Code: A

Tariff Record ID: 116

Tariff Record Collation Value: 	6065000

Tariff Record Parent Identifier: 2 Proposed Date: 2012-10-19 Priority Order:  600

Record Change Type:  Change 
Record Content Type:  2 
Associated Filing Identifier:  556

Service Agreement No. 1949

1

Service Agreement No. 1949

2

Service Agreement No. 1949

3

Service Agreement No. 1949

4

Service Agreement No. 1949

5

Service Agreement No. 1949

6

Service Agreement No. 1949

7

Service Agreement No. 1949

8

Service Agreement No. 1949

9

Service Agreement No. 1949

10

Service Agreement No. 1949

11

Service Agreement No. 1949

12

Service Agreement No. 1949

13

Service Agreement No. 1949

14

Service Agreement No. 1949

15

Service Agreement No. 1949

16

Service Agreement No. 1949

17

Service Agreement No. 1949

18

Service Agreement No. 1949

19

Service Agreement No. 1949

20

Service Agreement No. 1949

21

Service Agreement No. 1949

22

Service Agreement No. 1949

23

Service Agreement No. 1949

24

Service Agreement No. 1949

25

Service Agreement No. 1949

26

Service Agreement No. 1949

27

Service Agreement No. 1949

28

Service Agreement No. 1949

29

Service Agreement No. 1949

30

Service Agreement No. 1949

31

Service Agreement No. 1949

32

Service Agreement No. 1949

33

Service Agreement No. 1949

34

Service Agreement No. 1949

35

Service Agreement No. 1949

Preliminary Study Report - Alternative #2

Marcy Nanocenter 115kV Transmission Line Relocation

Prepared for:  Mohawk Valley EDGE

153 Brooks Road

Rome, NY 13441-4105

May, 2010

36

Service Agreement No. 1949

Marcy Nanocenter

Preliminary Study Report

Table of Contents

1.  BACKGROUND	3

2.  EXECUTIVE SUMMARY	3

3.  PROJECT OBJECTIVES	4

4.  EXISTING CONDITIONS	4

5.  PROPOSED ARRANGEMENT	4

6.  SCOPE OF WORK	5

7.  PROJECT DURATION	5

8.  SAFETY ASSESSMENT	5

9.  ENVIRONMENTAL ANALYSIS	5

10.  ENVIRONMENTAL REGULATORY LICENSING AND AGENCY REVIEW REQUIREMENTS	6

11.  EMF	7

12.  LOCAL PERMITTING	8

13.  RIGHT OF WAY	8

14.  SITE SERVICE STUDY	10

15.  COST ESTIMATE	11

16.  ATTACHMENTS	12

Site Photos

Map of Proposed Project Site

ROW Cross Section through all Three Lines

ROW Cross Section through One Line (Porter - Terminal #6) Electric Field Graph

Magnetic Field Graph

Detail Drawing - Single Circuit Steel Deadend Structure 
Detail Drawing - Single Circuit Suspension Wood Pole

2

37

Service Agreement No. 1949

Marcy Nanocenter

Preliminary Study Report

1.  Background

   In accordance with Mohawk Valley Edge’s request, National Grid hereby submits this

Preliminary  Study  Report	-  Alternative	#2  for  the  Marcy  Nanocenter	115kV  line

relocation.

o   This study was performed under a support services agreement between Mohawk 
	Valley Edge and National Grid.

o   This study determined the cost and schedule to relocate the 115kV Porter -
	Terminal #6 Line as close as possible to the existing Oneida - Porter #7 / 
	Yahnundasis - Porter #3 ROW and the edge of the Marcy Nanocenter property. 
	This approach maximizes the property available for development of the Marcy 
	Nanocenter site.

   Note:  This report provides an alternate approach (as requested by MVE) to the original 
	Preliminary Study Report dated November, 2009.

2.  Executive Summary

	National Grid has determined the following:

o 	The Porter - Terminal #6 Line that runs through the Marcy Nanocenter site can

be re-located to run along the existing ROW for the Oneida - Porter #7 and the Yahnundasis - Porter #3 Lines.  With current information known, there does not appear to be any difficulties in doing this work.

o 	No special line outages will be required to move the circuits, other than those

outages required to do line cutovers to existing energized circuits.

o 	Permitting and regulatory work will be required prior to construction.  These

requirements are not un-common or necessarily difficult to do, but do impact the project schedule and must be planned for.

o 	National Grid is willing to work with Mohawk Valley Edge (MVE) to accommodate

this move from a right of way perspective.  This assumes that MVE is willing to provide new right-of-way properties, as outlined below, to accommodate the relocated line.  In like fashion, National Grid will surrender the existing Porter -
Terminal #6 right-of-way property.  Note that with these adjustments, MVE must still deal with fiber optic cables (Verizon and Elantic) that currently follow the existing transmission lines and traverse the property.

o 	Environmental  assessments  performed  under  the  November  study,  did  not

produce any particularly unusual challenges from the information gathered.  It is 
anticipated that this will remain this way and that no significant wetlands, 
archeological, endangered species or other concerns will be encountered on this 
project.  This must be verified with additional analysis (delineation, involvement 
of agencies, etc).

o 	Electric and Magnetic field simulations show that future line relocation will be

below PSC established limits at the edges of the right-of-way.

o 	Schedule for doing this work is 27 months from contract agreements between

NG and MVE.  Approximately 8 months of this schedule are associated with the necessary  permitting  and  regulatory  approvals.  Note  that  there  may  be opportunities to improve upon this schedule (no permitting/regulatory problems encountered, running key activities in parallel, etc).

o 	Cost for doing this work is estimated at $5,220,000 (in 2009 dollars).  As with the

schedule, this is a conservative estimate that may be improved upon as more detailed engineering and analysis is performed.

3

38

Service Agreement No. 1949

Marcy Nanocenter

Preliminary Study Report

3.  Project Objectives

   The main objective of the project is to relocate the existing 115kV Porter - Terminal #6 
	Line which is located on Marcy Nanocenter’s property so that the property can be 
	developed.

   The Porter - Terminal #6 Line is to be relocated along the existing Oneida - Porter #7 
	and Yahnundasis - Porter #3 ROW.  The ROW may need to be expanded to provide 
	enough spacing between the lines.

   A new 100’ ROW will need to be developed at the western edge of the Marcy 
	Nanocenter site and the Porter - Terminal #6 Line will continue for about 3/4 of a mile 
	before reconnecting into the existing line.

   New structures will conform to National Grid Standards.  Conductors and shieldwires are 
	to be consistent with National Grid standards.

   Run an EMF check on the proposed spacing to make sure it meets code and does not 
	exceed reasonable levels.

   Perform a right of way and environmental assessment of site conditions with focus on 
	relocation of the NG lines.

   Provide a site service evaluation on how best to serve the Marcy Nanocenter site.

o   A cost estimate for this work will be created in a separate report, if requested by 
	the developer.

4.  Existing Conditions

   The 115kV line to be relocated is Porter - Terminal #6.  In the section to be relocated,

Porter	-  Terminal	#6  is  currently  supported  by  fourteen  single  circuit  wood  pole

structures, eleven suspension and three deadend, as shown in the table below.  The

length of the section to be removed is about 1 mile.

Structure Types	Number

Single Circuit 2-Pole Suspension Wood H-Frame Structure	11

Single Circuit 3-Pole Deadend Wood Pole Structure	3

Total	14

Existing Conductor Information

Conductor	795kcm ACSR “Drake”

5.  Proposed Arrangement

   The first mile of the relocated 115kV Porter - Terminal #6 Line will be within a shared 
	150’ ROW, with 50’ between the two structures.

   The Porter - Terminal #6 Line will continue for another 3/4 mile in a 100’ ROW, before 
	reconnecting into the existing line.  The new segment is to be supported by thirteen 
	single circuit, wood pole suspension structures with davit arms, and six single circuit,

4

39

Service Agreement No. 1949

Marcy Nanocenter

Preliminary Study Report

steel pole deadend structures.  The relocated segment of the Porter - Terminal #6 will span a total of 1 3/4 miles before connecting back into the existing line.

6.  Scope of Work

   Relocate the existing 115kV Porter - Terminal #6 Line into new ROW to run alongside 
	the Oneida - Porter #7 and Yahnundasis - Porter #3 Lines.  The line relocation will be 
	with the addition of nineteen new single circuit, single pole structures.

   Install new 795kcm ACSR “Drake” conductor and new 3/8” EHS shieldwire.

   Remove  the  existing  fourteen  structures  running  through  the  Marcy  Nanocenter 
	property.

7.  Project Duration

Phase	Start	Finish	Total Duration

Preliminary Engineering	1	2	2 Months

Detailed Design	2	5	3 Months

Procurement	5	11	6 Months

Permitting and Licensing	11	19	8 Months

Construction	19	25	6 Months

Closeout	25	27	2 Months

Project	1	27	27 Months

8.  Safety Assessment

   Design  and  construction  of  this  project  should  be  performed  in  accordance  with 
	applicable codes, regulations, bylaws and National Grid Standards. Construction of this 
	project will require work to be performed in close proximity to energized 115kV lines 
	during cutovers.

   The absence of any safety issues, not cited herein, does not exclude them from 
	possibility.

9.  Environmental Analysis

   A preliminary environmental analysis was performed during the site visits to the MVE 
	site. In addition, National Wetlands Inventory (NWI) and New York State Department of 
	Environmental  Conservation (NYSDEC)  databases  were  assessed  to  determine

potential issues that may be encountered due to project impacts to regulated wetlands and protected streams.  Field delineations of wetlands were not made.

   Based upon a review of these databases and the visual analysis performed, there are no 
	NYSDEC-regulated wetlands or protected streams that will be impacted by the project. 
	There is one unregulated stream within the southern portion of the project site that will 
	be crossed by the relocated Porter-Terminal #6 Line, but this should not be an issue. 
	Federal wetlands within the project area are mapped but these maps are not available 
	from online information sources. During the more extensive data gathering phase of the 
	project that will be required to support the licensing and permitting filings for the project,

5

40

Service Agreement No. 1949

Marcy Nanocenter

Preliminary Study Report

a right-of-way walkdown will be required to identify federal wetlands, if any, that may be impacted by the project.

10.  Environmental Regulatory Licensing and Agency Review Requirements

	Part 102 Report

o 	Pursuant to New York State Public Service Commission (NYSPSC) utility regulatory

requirements established in Title 16 of the Public Service Law, Part 102 - Installation 
of Non-Article VII Electric Transmission Facilities, any utility proposing to construct 
115 kV transmission facilities one mile or longer but less than ten miles in length 
must report the proposed construction to the NYSPSC at least 60 days before the 
proposed commencement of construction. The purpose of this reporting requirement 
is to afford the agency an opportunity to review the project to determine whether the 
transmission facility may be placed overhead or whether all or a portion of the facility 
should be placed underground. The “Part 102 Report” is also used to provide 
evidence   to   the   commission   that   NG  has  considered   and   addressed   key 
environmental and outreach areas and that the Company has complied with all 
applicable local, state and federal laws.

o	Areas that are typically addressed in the Part 102 filing include, but are not limited to:

Project Description and Need

Justification for Overhead Construction Community Outreach Activities

Environmental Issues/Impacts and Agency Consultation (New York State Office of Parks, Recreation and Historic Preservation; NYSDEC; US Fish & Wildlife Service; New York Natural Heritage Program; NYS Department of Agriculture and Markets

Project Aesthetics - potential requirement for a visual/view shed analysis

o 	The Part 102 report is typically prepared by an environmental consultant under

contract to NG’s Environmental Department.  Gathering of information and report 
preparation and filing are usually completed in 4-6 months. The NYSPSC review 
process is typically completed within 2-4 months following the filing of the report.

	New York State Office of Parks, Recreation and Historic Preservation (OPRHP)

o   Preliminary review of this project against OPRHP’s online database indicates that the 
	project will not impact any state or federal listed resources or resources eligible for 
	such listing. However, the project area is within a mapped Archaeological Sensitive 
	Area and consultation with OPRHP is recommended. Such consultation could result 
	in a requirement to complete an archaeological and cultural resource survey of the 
	project area (3-4 months to complete the report, submit to OPRHP, and obtain 
	OPRHP response).

	Stormwater Pollution Prevention Plan (SWPPP)

o   Total site disturbance associated with the relocated transmission line, transmission 
	line removals, and related activities will exceed the one acre threshold which triggers 
	the requirements of NYSDEC’s SWPPP program. Therefore, a SWPPP must be 
	prepared for this project and construction cannot begin until the SWPPP has been 
	completed, a Notice of Intent (NOI) form filed with the NYSDEC, and a SWPPP 
	acknowledgment letter received from the agency.  The SWPPP program will also

6

41

Service Agreement No. 1949

Marcy Nanocenter

Preliminary Study Report

require a pre-construction site inspection, weekly inspections over the duration of the construction period, a post-construction inspection and the filing of a Notice of Termination (NOT) form upon completion of construction and site restoration and stabilization. The SWPPP, NOI filing, and receipt of NYSDEC coverage letter typically can be completed within 3-4 months.

	NYSDEC Permits

o   As noted above, there do not appear to be any NYSDEC-regulated resources 
	impacted by the project, so NYSDEC permits for the project are not believed to be 
	required.

	US Army Corps of Engineers (ACOE)

o   Although the extent of the project impact on federal wetlands is not currently known, 
	such impacts, if any, will be identified during the information gathering that is 
	required to prepare the Part 102 report and the SWPPP.  Typically, such impacts are 
	small and project impacts would be tailored in accordance with NG’s environmental 
	guidance procedures (i.e. use of appropriate erosion and sediment controls, no 
	permanent fill in wetlands, use of swamp mats or other suitable temporary methods 
	to cross wetlands, restoration of disturbed areas to pre-construction conditions, etc.) 
	so as to avoid ACOE permitting requirements.

	Other Agencies

o   Other environmental agencies including the NYS Department of Agriculture and 
	Markets, the NYSDEC’s New York Natural Heritage Program, and the US Fish & 
	Wildlife Service may be contacted to determine, respectively, whether the project 
	may impact sensitive agricultural areas and state- or federal-listed threatened or 
	endangered  species.  Although  these agencies  do  not have  specific  permitting 
	authority, evidence of agency consultation is required as part of the NYSPSC and 
	ACOE  review and  SWPPP  preparation  process.  If  project-related  impacts  are 
	identified, appropriate measures will be incorporated into the project design and 
	construction to mitigate the identified impacts.

11.  EMF

   Electric and magnetic field levels were calculated at the New York state standard height 
	of one meter above ground level at the edge of right of way, using the PLS-CADD EMF 
	calculator.  These calculations are based upon EPRI “red book” methods.

   All calculations were based upon winter normal loading conditions (1500 amps Drake 
	conductor)

   For the line configuration modeled (graphs shown in the appendix of this report) both the 
	electric and magnetic field are below the NYS PSC edge of right of way requirements of

1.6 kV/m (electric) and 200 mG (magnetic).

   As can be seen by looking at the graph, the EMF values continue to “trail off” past the 
	edge of the right of way.  These low values will be key to attracting chip fabrication 
	industry to this site.

7

42

Service Agreement No. 1949

Marcy Nanocenter

Preliminary Study Report

12.  Local Permitting

   No formal assessment has been done.  As a part of any construction on any site, local 
	permitting requirements must be adhered to.  Specific zoning requirements and local 
	building codes may control design and construction on the site.  Due to the fact that 
	transmission structures are all ready present on the site, this is not for-seen as a 
	problem; however local requirements must be investigated and may come into play.

13.  Right of Way

	The right-of-way work for the Marcy Site falls into two categories.  That right-of-way that

will need to be widened to relocate the existing 115kV Porter - Terminal #6 Line and the 100’ right-of-way that will be developed to the west side of the Marcy Site (Marcy Site Relocation Right-of-Way).  New right-of-way will also be required for two new 115kV lines that are needed to provide dual service to the customer owned station (Marcy Site New Service Right-of-Way).

	Marcy Site Relocation Right-of-Way

o 	To accommodate the proposed 115kV relocations a combination of fee and easement

right-of-way must be conveyed to Niagara Mohawk Power Corporation (NG) in order to 
replace ‘like with like” property rights. Currently the double circuit Oneida-Porter #7 / 
Yahnundasis-Porter #3 Line (#7/#3 Line) occupies a 100 foot wide fee owned right-of-
way (Tax Parcel 293-1-80, Town of Marcy) and the single circuit Porter-Terminal #6 Line 
occupies a 100 foot wide easement. A fee strip will be required for only that portion of 
the relocation that includes the #7/#3 Line as shown on attached Exhibit SUP-A. It will 
be necessary for the new fee strip to expand the existing ROW to 150 feet in width since 
the right-of-way for this portion of the relocation must accommodate the existing 115 kV 
double circuit and single circuit structures (see attached cross sections). As shown on 
Exhibit SUP-A, the remaining portion of the relocation right-of-way will be a 100 foot 
wide  easement  strip  which  will  accommodate  one  single  circuit  structure.  Both 
instruments (deeds and easements) will be required to have additional language to 
cover “guying rights” and “danger tree rights” outside the primary strip. It is noted that 
there are two alternatives shown for the easement portion of the right-of-way. The 
shorter alternative “B” is located entirely on the Marcy Site while the longer alternative 
“A” would leave the Marcy Site and traverse private property to the south. The shorter 
“B” alternative was shown in the event that MARCY NANOCENTER decides not to 
attempt to acquire easement rights from private landowners. The longer “A” alternative 
was the route used for purposes of the cost estimate.

o 	For the purposes of this report, it is assumed that MVE will acquire all fee parcels and

easements  and  convey  all  fee  parcels  and  easements  to  NG  at  no  cost.  NG 
administrative, legal and closing costs are included in the estimated cost. National Grid 
will release any portions of the existing easements across MVE property that are no 
longer necessary as a result of the relocations. NG will retain title of the existing 100 foot 
wide fee strip unless MARCY NANOCENTER arranges to have the two buried fiber optic 
cables (Elantic and Verizon) that currently occupy the existing fee strip moved to the 
new fee strip.

8

43

Service Agreement No. 1949

Marcy Nanocenter

Preliminary Study Report

   Marcy Site New Service Right-of-Way

   As noted in the site service study section of this report, two alternatives have been 
	considered to provide dual 115kV service to the Marcy Site. Both alternatives require 
	obtaining right-of-way from private landowners along the entire length of the respective 
	routes. The right-of-way requirements for either of the alternatives, and for any other 
	alternatives that might be considered in the future, will be a 100 foot wide easement in 
	locations where one line occupies the right-of-way and a 150 foot wide easement in 
	locations where two lines occupy the right-of-way. The easement instruments will be 
	required to have additional language to cover “guying rights” and “danger tree rights” 
	outside the primary strip. If MVE determines to select either of these alternatives, it is 
	assumed that MVE will procure all necessary easement rights as required by NG and 
	convey those rights to NG at no cost.

EXHIBIT SUP-A

EXISTING

#3 / #7 LINES

EXISTING 
#6 LINE

OPTION B

OPTION A

9

44

Service Agreement No. 1949

Marcy Nanocenter

Preliminary Study Report

14.  Site Service Study

	Study Overview

o 	National Grid has undertaken a preliminary planning review of likely alternatives to

provide redundant 115kV service to a 50 MVA load at the Marcy Site. This work will be additional and is not included in the cost estimate.  To provide this redundant service, two separate pathways would be required, including separate structures, to avoid the potential for a single failure removing both services simultaneously. National Grid has identified three likely alternatives, which are outlined as follows:

	Option 1:

o 	Option 1 includes two single 115 kV line taps, originating at Porter Substation, which

would serve just the Marcy Site.  An individual breaker would serve each line at Porter. Each line would be a dedicated feed to the project site.  It is anticipated that this solution would require new RIGHT-of-Way (ROW) and new structures between Porter and the Marcy Site for one of the lines; and for the second line, removal of the existing PorterTerminal H-frame structures, and replacement with a double circuit towers. All this would have to be accomplished in an area already congested with existing ROW and limited egress. An investigation into potential availability of property for new ROW would have to be conducted before this option could be selected.

	Option 2:

o 	Option 2 has one single line tap at a breaker position originating at Porter Substation,

similar to those proposed in Option 1, plus an additional tap from the (to be relocated) 115kV Porter-Terminal transmission circuit. This would again provide two separate and independent services. There would still be a need to install new towers for the Porter tap, plus an additional single breaker station will be needed at the Marcy Site to handle the additional line tap. This option may require new ROW as in Option 1.

	Option 3:

o 	Option 3 would split the existing Porter-Terminal 115kV line into two parts, there by

making one line into two and providing redundant service from two directions. A new 
station with a 3 breaker ring configuration would be constructed on the Marcy Site at the 
split point.  With this configuration, one end of the line can be out of service, while other 
would still remain to serve the Nanocenter. With Option 3 most, if not all, work would be 
located on the Marcy Site, and not involve other existing ROW or outside property 
owners.

	Recommendation:

o 	It is National Grid’s current recommendation that Option 3 to pursued. Since the work is

primarily limited to the Marcy Site, this provides for better project transparency and control. And this avoids the potential property/political issues associated with ROW expansion and/or expansion on our existing ROW.

	Disclaimer:

o	The cost estimate included in this Preliminary Study Report is for the Porter - Terminal

#6 Line relocation only.

o	A cost estimate for completing this Nanocenter Site Service will be completed in a

separate report if requested by Marcy Edge.

10

45

Service Agreement No. 1949

Marcy Nanocenter

Preliminary Study Report

15.  Cost Estimate

	The following represents National Grid estimate to do the following work:

o   Relocate the existing Porter - Terminal #6 Line between structure number 12 and

26. The new segment is to be supported by nineteen single circuit structures.  Six 
single  steel  pole  deadend  structures  and  thirteen  wood  pole  suspensions 
structures will run parallel to the Oneida - Porter #7 and Yahnundasis - Porter #3 
Lines on an expanded ROW.  The ROW will have to be widened to provide 
enough spacing between lines.  The Porter - Terminal #6 Line will continue by 
itself for another 3/4 mile on a 100 foot ROW, before reconnecting into the

existing line.

	Estimate assumptions:

o	No right-of-way “real property” cost.  Lands will be transferred between National

Grid and Marcy Nanocenter for consideration of 1 dollar.  Costs are included for

labor associated with land transfers, closing costs and legal costs.

o	All cost estimates in 2009 dollars.  No escalation included.

o	Allowance  for  funds  used  during  construction	(AFUDC)  charges  are  NOT

included in these costs, because NG is assuming that upfront payments will be 
made by MVE.  AFUDC charges represent interest on monies that National Grid 
“borrows” to fund our projects and represent a relatively large amount of the total 
amount.  Accordingly to avoid these charges, prompt payments must be made by 
MVE to NG.

o	It is assumed that the Marcy Nanocenter project is tax exempt.

o	Project costs estimates are conceptual in nature.  It is likely that this amount can

be reduced further with more detailed engineering, site investigation, wetland

delineation, permitting etc is performed.

o	Lines will be worked on concurrently, except during cutovers.

o	No environmental cleanup will be required.

o	Estimates assume that a filing is required under NYS PSC Part 102.  Costs for

this filing are included in the estimate.

o	No special local permitting required (i.e. zoning variance, subdivisions, etc).

Costs are included to attend local planning board meetings with towns.	(2

meetings)

o	This estimate is based on the project taking 27 months from start of preliminary

engineering until final closeout.

o	Site Service Study will be a separate project, and is not included in this estimate.

Project Edge

Summary - Cost Breakdown

Labor, Expenses and Fringes	$	2,740,000.00

Materials and Handling	$	570,000.00

Transportation	$	20,000.00

Overheads	$	680,000.00

SUB TOTAL	$	4,010,000.00

Sales Tax (0%)	$	-

SUB TOTAL	$	4,010,000.00

Contingency (30%)	$	1,210,000.00

TOTAL	$	5,220,000.00

11

46

Service Agreement No. 1949

Marcy Nanocenter

Preliminary Study Report

16.  Attachments

Site Photos

Image #1:  From Hazard Road	Image #2:  From Hazard Road

Looking Towards Nanocenter Site	Looking Towards Porter Substation

Image #3:  Double Circuit Steel Flex Tower

12

47

Service Agreement No. 1949

MARCY 115kV RELOCATION

EXISTING #3/#7 ROW

TO BE EXPANDED

NEW #6 ROW	EXISTING #6 ROW

SINGLE CIRCUIT DEADEND STRUCTURE

SINGLE CIRCUIT SUSPENSION STRUCTURE PROPOSED ROW

NEW 115kV LINE

EXISTING 115kV LINES

PROPOSED PROJECT SITE

48

Service Agreement No. 1949

49

Service Agreement No. 1949

50

Service Agreement No. 1949

ELECTRIC FIELD PROFILE - MARCY 115KV RELOCATION

3.5

115kV Oneida - Porter #7

115kV Yahnundasis - Porter #3

Conductor: 795kcmil ACSR "DRAKE"

3

2.5

2

1.5

1

0.5

0

0

115kV Porter - Terminal #6 
Conductor: 795kcmil ACSR "DRAKE"

Winter Normal Rating: 1395A 
	Min Midspan Clearance: 23'

1

3

2

50' to edge of ROW

10	20	30	40	50	60	70

Winter Normal Rating: 1395A 
	Min Midspan Clearance: 23'

1	1

3	3

2	2

50'	50' to edge of ROW

80	90	100	110	120	130	140	150

ROW (feet)

Based on the State of New York, Public Safety Comission, Statement of Interim Policu on Magnetic Fields of Major Electric Transmission Facilities: Electric Field @ Winter Normal Load: 1.6kV/m @ edge ROW

Electric Field (kV/m)

Edge of ROW

Edge of ROW

51

Service Agreement No. 1949

MAGNETIC FIELD PROFILE - MARCY 115KV RELOCATION

450

115kV Oneida - Porter #7

115kV Yahnundasis - Porter #3

400

350

300

250

200

150

100

50

0

0

115kV Porter - Terminal #6 
Conductor: 795kcmil ACSR "DRAKE"

Winter Normal Rating: 1395A 
	Min Midspan Clearance: 23'

1

3

2

50' to edge of ROW

10	20	30	40	50	60	70

Conductor: 795kcmil ACSR "DRAKE" 
	Winter Normal Rating: 1395A

Min Midspan Clearance: 23'

1	1

3	3

2	2

50'	50' to edge of ROW

80	90	100	110	120	130	140	150

ROW (feet)

Based on the State of New York, Public Safety Comission, Statement of Interim Policu on Magnetic Fields of Major Electric Transmission Facilities: Magnetic Field @ Winter Normal Load: 200mG @ edge ROW

Magnetic Field (mG)

Edge of ROW

Edge of ROW

52

Service Agreement No. 1949

53

Service Agreement No. 1949

54

Service Agreement No. 1949

55

Service Agreement No. 1949

56

Service Agreement No. 1949

57

Service Agreement No. 1949

58

Service Agreement No. 1949

59

Service Agreement No. 1949

60

Service Agreement No. 1949

61

Service Agreement No. 1949

62

Service Agreement No. 1949

63

Service Agreement No. 1949

64

Service Agreement No. 1949

65

Service Agreement No. 1949

66

Service Agreement No. 1949

67

Service Agreement No. 1949

68

Service Agreement No. 1949

69

Service Agreement No. 1949

70

Service Agreement No. 1949

71

Service Agreement No. 1949

72

Service Agreement No. 1949

73

Service Agreement No. 1949

74

Service Agreement No. 1949

75

Service Agreement No. 1949

76

Service Agreement No. 1949

77

Service Agreement No. 1949

78

Service Agreement No. 1949

79

Service Agreement No. 1949

80